## Toolkit Settings
Parameter Name | Modbus Function | Register High | Register Low | Data Type
UPS status | Read Holding Registers | 0 | 40002 | Unsigned 16 bit Integer
Bypass | Read Holding Registers | 0 | 40003 | Unsigned 16 bit Integer
Energy Storage 1 | Read Holding Registers | 0 | 40004 | Unsigned 16 bit Integer
Energy Storage 2 | Read Holding Registers | 0 | 40005 | Unsigned 16 bit Integer
General 1 | Read Holding Registers | 0 | 40006 | Unsigned 16 bit Integer
General 2 | Read Holding Registers | 0 | 40007 | Unsigned 16 bit Integer
General 3 | Read Holding Registers | 0 | 40008 | Unsigned 16 bit Integer
General 4 | Read Holding Registers | 0 | 40009 | Unsigned 16 bit Integer
Reserved 1 | Read Holding Registers | 0 | 40010 | Unsigned 16 bit Integer
Reserved 2 | Read Holding Registers | 0 | 40011 | Unsigned 16 bit Integer
Input | Read Holding Registers | 0 | 40012 | Unsigned 16 bit Integer
Output | Read Holding Registers | 0 | 40013 | Unsigned 16 bit Integer
Parallel system | Read Holding Registers | 0 | 40014 | Unsigned 16 bit Integer
Power module | Read Holding Registers | 0 | 40015 | Unsigned 16 bit Integer
Reserved 3 | Read Holding Registers | 0 | 40016 | Unsigned 16 bit Integer
Static bypass switch | Read Holding Registers | 0 | 40017 | Unsigned 16 bit Integer
Switchgear 1 | Read Holding Registers | 0 | 40018 | Unsigned 16 bit Integer
Switchgear 2 | Read Holding Registers | 0 | 40019 | Unsigned 16 bit Integer
System level controller - SLC | Read Holding Registers | 0 | 40020 | Unsigned 16 bit Integer
Unit Controller - UC | Read Holding Registers | 0 | 40021 | Unsigned 16 bit Integer
Battery Charger | Read Holding Registers | 0 | 40022 | Unsigned 16 bit Integer
Energy Storage | Read Holding Registers | 0 | 40023 | Unsigned 16 bit Integer
Network | Read Holding Registers | 0 | 40024 | Unsigned 16 bit Integer
UPS Battery Timer Stats Reset min | Read Holding Registers | 44210 | 44209 | Unsigned 32 bit Integer
UPS Batt. Operation Time Since Reset min | Read Holding Registers | 44212 | 44211 | Unsigned 32 bit Integer
UPS Time OP Stats Since Timer Reset min | Read Holding Registers | 44214 | 44213 | Unsigned 32 bit Integer
UPS Time Normal Since Timer Reset min | Read Holding Registers | 44216 | 44215 | Unsigned 32 bit Integer
UPS Time Bypass Since Timer Reset min | Read Holding Registers | 44218 | 44217 | Unsigned 32 bit Integer
UPS Time ECOnversion Since Reset min | Read Holding Registers | 44220 | 44219 | Unsigned 32 bit Integer
UPS Time Since Battery Replaced min | Read Holding Registers | 44222 | 44221 | Unsigned 32 bit Integer
UPS Time Since Energy IN Timer Reset min | Read Holding Registers | 44224 | 44223 | Unsigned 32 bit Integer
UPS Time Since Energy O Timer Reset min | Read Holding Registers | 44226 | 44225 | Unsigned 32 bit Integer
Phase A Apparent Output Power kVA | Read Holding Registers | 0 | 44865 | Unsigned 16 bit Integer
Phase B Apparent Output Power kVA | Read Holding Registers | 0 | 44866 | Unsigned 16 bit Integer
Phase C Apparent Output Power kVA | Read Holding Registers | 0 | 44867 | Unsigned 16 bit Integer
Phase A Output Current A | Read Holding Registers | 0 | 44868 | Unsigned 16 bit Integer
Phase B Output Current A | Read Holding Registers | 0 | 44869 | Unsigned 16 bit Integer
Phase C Output Current A | Read Holding Registers | 0 | 44870 | Unsigned 16 bit Integer
Phase A Output Crest Factor | Read Holding Registers | 0 | 44871 | Unsigned 16 bit Integer
Phase B Output Crest Factor | Read Holding Registers | 0 | 44872 | Unsigned 16 bit Integer
Phase C Output Crest Factor | Read Holding Registers | 0 | 44873 | Unsigned 16 bit Integer
Phase A Output THD % | Read Holding Registers | 0 | 44874 | Unsigned 16 bit Integer
Phase B Output THD % | Read Holding Registers | 0 | 44875 | Unsigned 16 bit Integer
Phase C Output THD % | Read Holding Registers | 0 | 44876 | Unsigned 16 bit Integer
Phase A Output Power Factor | Read Holding Registers | 0 | 44877 | Unsigned 16 bit Integer
Phase B Output Power Factor | Read Holding Registers | 0 | 44878 | Unsigned 16 bit Integer
Phase C Output Power Factor | Read Holding Registers | 0 | 44879 | Unsigned 16 bit Integer
Phase A Output Real Power kW | Read Holding Registers | 0 | 44880 | Unsigned 16 bit Integer
Phase B Output Real Power kW | Read Holding Registers | 0 | 44881 | Unsigned 16 bit Integer
Phase C Output Real Power kW | Read Holding Registers | 0 | 44882 | Unsigned 16 bit Integer
Phase A Output Voltage V | Read Holding Registers | 0 | 44883 | Unsigned 16 bit Integer
Phase B Output Voltage V | Read Holding Registers | 0 | 44884 | Unsigned 16 bit Integer
Phase C Output Voltage V | Read Holding Registers | 0 | 44885 | Unsigned 16 bit Integer
Phase A-B Output Voltage V | Read Holding Registers | 0 | 44886 | Unsigned 16 bit Integer
Phase B-C Output Voltage V | Read Holding Registers | 0 | 44887 | Unsigned 16 bit Integer
Phase C-A Output Voltage V | Read Holding Registers | 0 | 44888 | Unsigned 16 bit Integer
Total Apparent Output Power kVA | Read Holding Registers | 0 | 44889 | Unsigned 16 bit Integer
Percent of Highest Output Current % | Read Holding Registers | 0 | 44890 | Unsigned 16 bit Integer
Output Frequency Hz | Read Holding Registers | 0 | 44891 | Unsigned 16 bit Integer
Total Real Output Power kW | Read Holding Registers | 0 | 44892 | Unsigned 16 bit Integer
Cumulative Energy Supplied kWh | Read Holding Registers | 44894 | 44893 | Unsigned 32 bit Integer
Phase N Output Current A | Read Holding Registers | 0 | 44895 | Unsigned 16 bit Integer
Phase A Apparent Input Power kVA | Read Holding Registers | 0 | 45121 | Unsigned 16 bit Integer
Phase B Apparent Input Power kVA | Read Holding Registers | 0 | 45122 | Unsigned 16 bit Integer
Phase C Apparent Input Power kVA | Read Holding Registers | 0 | 45123 | Unsigned 16 bit Integer
Phase A Input Current A | Read Holding Registers | 0 | 45124 | Unsigned 16 bit Integer
Phase B Input Current A | Read Holding Registers | 0 | 45125 | Unsigned 16 bit Integer
Phase C Input Current A | Read Holding Registers | 0 | 45126 | Unsigned 16 bit Integer
Phase A Input Power Factor | Read Holding Registers | 0 | 45127 | Unsigned 16 bit Integer
Phase B Input Power Factor | Read Holding Registers | 0 | 45128 | Unsigned 16 bit Integer
Phase C Input Power Factor | Read Holding Registers | 0 | 45129 | Unsigned 16 bit Integer
Phase A Input Real Power kW | Read Holding Registers | 0 | 45130 | Unsigned 16 bit Integer
Phase B Input Real Power kW | Read Holding Registers | 0 | 45131 | Unsigned 16 bit Integer
Phase C Input Real Power kW | Read Holding Registers | 0 | 45132 | Unsigned 16 bit Integer
Phase A Input Voltage V | Read Holding Registers | 0 | 45133 | Unsigned 16 bit Integer
Phase B Input Voltage V | Read Holding Registers | 0 | 45134 | Unsigned 16 bit Integer
Phase C Input Voltage V | Read Holding Registers | 0 | 45135 | Unsigned 16 bit Integer
Phase A-B Input Voltage V | Read Holding Registers | 0 | 45136 | Unsigned 16 bit Integer
Phase B-C Input Voltage V | Read Holding Registers | 0 | 45137 | Unsigned 16 bit Integer
Phase C-A Input Voltage V | Read Holding Registers | 0 | 45138 | Unsigned 16 bit Integer
Total Apparent Input Power kVA | Read Holding Registers | 0 | 45139 | Unsigned 16 bit Integer
Input Frequency Hz | Read Holding Registers | 0 | 45140 | Unsigned 16 bit Integer
Total Real Input Power kW | Read Holding Registers | 0 | 45141 | Unsigned 16 bit Integer
Cumulative Energy Consumption kWh | Read Holding Registers | 45143 | 45142 | Unsigned 32 bit Integer
Phase A Apparent Bypass Input Power kVA | Read Holding Registers | 0 | 45377 | Unsigned 16 bit Integer
Phase B Apparent Bypass Input Power kVA | Read Holding Registers | 0 | 45378 | Unsigned 16 bit Integer
Phase C Apparent Bypass Input Power kVA | Read Holding Registers | 0 | 45379 | Unsigned 16 bit Integer
Phase A Input Current Bypass A | Read Holding Registers | 0 | 45380 | Unsigned 16 bit Integer
Phase B Input Current Bypass A | Read Holding Registers | 0 | 45381 | Unsigned 16 bit Integer
Phase C Input Current Bypass A | Read Holding Registers | 0 | 45382 | Unsigned 16 bit Integer
Phase A Input Bypass Power Factor | Read Holding Registers | 0 | 45383 | Unsigned 16 bit Integer
Phase B Input Bypass Power Factor | Read Holding Registers | 0 | 45384 | Unsigned 16 bit Integer
Phase C Input Bypass Power Factor | Read Holding Registers | 0 | 45385 | Unsigned 16 bit Integer
Phase A Input Real Bypass Power kW | Read Holding Registers | 0 | 45386 | Unsigned 16 bit Integer
Phase B Input Real Bypass Power kW | Read Holding Registers | 0 | 45387 | Unsigned 16 bit Integer
Phase C Input Real Bypass Power kW | Read Holding Registers | 0 | 45388 | Unsigned 16 bit Integer
Phase A Input Bypass Voltage V | Read Holding Registers | 0 | 45389 | Unsigned 16 bit Integer
Phase B Input Bypass Voltage V | Read Holding Registers | 0 | 45390 | Unsigned 16 bit Integer
Phase C Input Bypass Voltage V | Read Holding Registers | 0 | 45391 | Unsigned 16 bit Integer
Phase A-B Input Bypass Voltage V | Read Holding Registers | 0 | 45392 | Unsigned 16 bit Integer
Phase B-C Input Bypass Voltage V | Read Holding Registers | 0 | 45393 | Unsigned 16 bit Integer
Phase C-A Input Bypass Voltage V | Read Holding Registers | 0 | 45394 | Unsigned 16 bit Integer
Total Apparent Input Bypass Power kVA | Read Holding Registers | 0 | 45395 | Unsigned 16 bit Integer
Input Bypass Frequency Hz | Read Holding Registers | 0 | 45396 | Unsigned 16 bit Integer
Total Real Input Bypass Power kW | Read Holding Registers | 0 | 45397 | Unsigned 16 bit Integer
Battery Highest Temperature Celsius | Read Holding Registers | 0 | 45634 | Unsigned 16 bit Integer
Battery Power Drawn kW | Read Holding Registers | 0 | 45635 | Unsigned 16 bit Integer
Battery Low Volt. Shutdown Est. Time Sec | Read Holding Registers | 45638 | 45637 | Unsigned 32 bit Integer
Battery Recharge Estimated Time Sec | Read Holding Registers | 45640 | 45639 | Unsigned 32 bit Integer
Battery Charge Percentage % | Read Holding Registers | 0 | 45641 | Unsigned 16 bit Integer
Battery Voltage V | Read Holding Registers | 0 | 45642 | Unsigned 16 bit Integer
Battery Current Drawn A | Read Holding Registers | 0 | 45643 | Unsigned 16 bit Integer
Battery Total Energy Capacity Ah | Read Holding Registers | 0 | 45647 | Unsigned 16 bit Integer
Phase A-B Input Current A | Read Holding Registers | 0 | 46145 | Unsigned 16 bit Integer
Phase B-C Input Current A | Read Holding Registers | 0 | 46146 | Unsigned 16 bit Integer
Phase C-A Input Current A | Read Holding Registers | 0 | 46147 | Unsigned 16 bit Integer
Phase A-B Bypass Current A | Read Holding Registers | 0 | 46148 | Unsigned 16 bit Integer
Phase B-C Bypass Current A | Read Holding Registers | 0 | 46149 | Unsigned 16 bit Integer
Phase C-A Bypass Current A | Read Holding Registers | 0 | 46150 | Unsigned 16 bit Integer
Phase A-B Output Current A | Read Holding Registers | 0 | 46151 | Unsigned 16 bit Integer
Phase B-C Output Current A | Read Holding Registers | 0 | 46152 | Unsigned 16 bit Integer
Phase C-A Output Current A | Read Holding Registers | 0 | 46153 | Unsigned 16 bit Integer
Total Parallel Apparent Output Power kVA | Read Holding Registers | 0 | 46154 | Unsigned 16 bit Integer
Usage of UPS System Capacity % | Read Holding Registers | 0 | 46155 | Unsigned 16 bit Integer
Total Active Output Power kW | Read Holding Registers | 0 | 46156 | Unsigned 16 bit Integer
Temperature Sensor °C | Read Holding Registers | 0 | 46401 | Unsigned 16 bit Integer
Humidity Sensor % RH | Read Holding Registers | 0 | 46402 | Unsigned 16 bit Integer
Transfer Current Ramp-in Timer Sec | Read Holding Registers | 0 | 48195 | Unsigned 16 bit Integer
Voltage Compensation % | Read Holding Registers | 0 | 48198 | Unsigned 16 bit Integer
UPS Apparent Power Rating kVA | Read Holding Registers | 0 | 48200 | Unsigned 16 bit Integer
Acceptable Percent of Nominal Voltage % | Read Holding Registers | 0 | 48201 | Unsigned 16 bit Integer
Set Output Overload Status Threshold % | Read Holding Registers | 0 | 48203 | Unsigned 16 bit Integer
Charger Current Rate User Settings | Read Holding Registers | 0 | 48205 | Unsigned 16 bit Integer
Minimum Allow Tempurature Setting °C | Read Holding Registers | 0 | 48210 | Unsigned 16 bit Integer
Maximum Allow Tempurature Setting °C | Read Holding Registers | 0 | 48211 | Unsigned 16 bit Integer
Battery Test Sched. Time of Day Sec | Read Holding Registers | 48215 | 48214 | Unsigned 32 bit Integer
Transformer Voltage Drop Compensation % | Read Holding Registers | 0 | 48219 | Unsigned 16 bit Integer
Asynch. Bypass Brk Duration Setting ms | Read Holding Registers | 0 | 48220 | Unsigned 16 bit Integer
Charging Capacity from System Rated kW % | Read Holding Registers | 0 | 48221 | Unsigned 16 bit Integer
UPS Modular Battery Cabinets | Read Holding Registers | 0 | 48222 | Unsigned 16 bit Integer
Parallel UPS Number of the Operated UPS | Read Holding Registers | 0 | 48223 | Unsigned 16 bit Integer
Parallel UPS Min. Avail. for Autostart | Read Holding Registers | 0 | 48226 | Unsigned 16 bit Integer
UPS Real Power Rating kW | Read Holding Registers | 0 | 48228 | Unsigned 16 bit Integer

## Table001 (Page 1-19)
1 | 2 | 3 | 4 | 5 | Original Name | Adjusted Name | Char Length | Parameter Name | Modbus Function | Register High | Register Low | Data Type | Column6 | BOOLEAN | Column8 | Column9 | Column10
|  |  | 0 |  |  | 0 | 1 | 0 |  | 0 |  |  |  |  | Scale
Modicon Standard Register Number | Absolute Starting Register Address (Hexa-decimal) | 0 | 0 | Bit | Data Point | Data Point | 25 | Data Point Valid Response |  | 0 | 40001 |  | Length | Data Type | Multiply Reading By | Divide Reading By | Valid Response
Status Data |  |  | 0 |  |  |  | 0 |  |  | 0
40002 | 0x0001 | 1 | 0 |  | UPS status | UPS status | 10 | UPS status | Read Holding Registers | 0 | 40002 | Unsigned 16 bit Integer | 1 | BOOLEAN
|  |  | 0 | 0 | UPS operation mode - Battery | UPS operation mode - Battery | TOO LONG | UPS operation mode - Battery 1=UPS operation mode - Battery |  | 0 |  |  |  | BOOLEAN |  |  | 1=UPS operation mode - Battery
|  |  | 0 | 1 | Battery is below minimum acceptable runtime | Battery is below minimum acceptable runtime | TOO LONG | Battery is below minimum acceptable runtime 1=Battery is below minimum acceptable runtime |  | 0 |  |  |  | BOOLEAN |  |  | 1=Battery is below minimum acceptable runtime
|  |  | 0 | 2 | Bypass | Bypass | 25 | Bypass 1=UPS is in bypass |  | 0 |  |  |  | BOOLEAN |  |  | 1=UPS is in bypass
|  |  | 0 | 3 | UPS operation mode - Battery test | UPS operation mode - Battery test | TOO LONG | UPS operation mode - Battery test 1=UPS operation mode - Battery test |  | 0 |  |  |  | BOOLEAN |  |  | 1=UPS operation mode - Battery test
|  |  | 0 | 4 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 5 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 6 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 7 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 8 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 9 | Battery inoperable | Battery inoperable | 39 | Battery inoperable 1=Battery inoperable |  | 0 |  |  |  | BOOLEAN |  |  | 1=Battery inoperable
|  |  | 0 | 10 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 11 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 12 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 13 | Informational alarm present | Informational alarm present | TOO LONG | Informational alarm present 1=Informational alarm present |  | 0 |  |  |  | BOOLEAN |  |  | 1=Informational alarm present
|  |  | 0 | 14 | Warning alarm present | Warning alarm present | TOO LONG | Warning alarm present 1=Warning alarm present |  | 0 |  |  |  | BOOLEAN |  |  | 1=Warning alarm present
|  |  | 0 | 15 | Critical alarm present | Critical alarm present | TOO LONG | Critical alarm present 1=Critical alarm present |  | 0 |  |  |  | BOOLEAN |  |  | 1=Critical alarm present
Alarm Register |  |  | 0 |  |  |  | 0 |  |  | 0
40003 | 0x0002 | 2 | 0 |  | Bypass | Bypass | 6 | Bypass | Read Holding Registers | 0 | 40003 | Unsigned 16 bit Integer | 1 | BOOLEAN
|  |  | 0 | 0 | Bypass voltage out of tolerance | Bypass voltage out of tolerance | TOO LONG | Bypass voltage out of tolerance 1=Bypass voltage is out of tolerance and UPS is prevented from going into requested bypass mode |  | 0 |  |  |  | BOOLEAN |  |  | 1=Bypass voltage is out of tolerance and UPS is prevented from going into requested bypass mode
|  |  | 0 | 1 | Bypass phase sequence incorrect | Bypass phase sequence incorrect | TOO LONG | Bypass phase sequence incorrect 1=The phase rotation on bypass is incorrect |  | 0 |  |  |  | BOOLEAN |  |  | 1=The phase rotation on bypass is incorrect
|  |  | 0 | 2 | Bypass frequency out of tolerance | Bypass frequency out of tolerance | TOO LONG | Bypass frequency out of tolerance 1=Bypass frequency is out of tolerance |  | 0 |  |  |  | BOOLEAN |  |  | 1=Bypass frequency is out of tolerance
|  |  | 0 | 3 | Bypass phase missing | Bypass phase missing | TOO LONG | Bypass phase missing 1=Bypass is missing a phase |  | 0 |  |  |  | BOOLEAN |  |  | 1=Bypass is missing a phase
|  |  | 0 | 4 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 5 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 6 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 7 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 8 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 9 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 10 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 11 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 12 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 13 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 14 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 15 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
40004 | 0x0003 | 3 | 0 |  | Energy storage | Energy Storage 1 | 16 | Energy Storage 1 | Read Holding Registers | 0 | 40004 | Unsigned 16 bit Integer | 1 | BOOLEAN
|  |  | 0 | 0 | Battery breaker BB1 open | Battery breaker BB1 open | TOO LONG | Battery breaker BB1 open 1=Battery breaker BB1 is open |  | 0 |  |  |  | BOOLEAN |  |  | 1=Battery breaker BB1 is open
|  |  | 0 | 1 | Battery breaker BB2 open | Battery breaker BB2 open | TOO LONG | Battery breaker BB2 open 1=Battery breaker BB2 is open |  | 0 |  |  |  | BOOLEAN |  |  | 1=Battery breaker BB2 is open
|  |  | 0 | 2 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 3 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 4 | Batteries are discharging | Batteries are discharging | TOO LONG | Batteries are discharging 1=The load is drawing more power than the UPS can draw from the input, causing the UPS to draw power from the batteries |  | 0 |  |  |  | BOOLEAN |  |  | 1=The load is drawing more power than the UPS can draw from the input, causing the UPS to draw power from the batteries
|  |  | 0 | 5 | Charger shutdown due to high battery temperature | Charger shutdown due to high battery temperature | TOO LONG | Charger shutdown due to high battery temperature 1=The charger has been shut down due to a high battery temperature |  | 0 |  |  |  | BOOLEAN |  |  | 1=The charger has been shut down due to a high battery temperature
|  |  | 0 | 6 | Battery is below minimum acceptable runtime | Battery is below minimum acceptable runtime | TOO LONG | Battery is below minimum acceptable runtime 1=The battery runtime is below configured minimum acceptable value |  | 0 |  |  |  | BOOLEAN |  |  | 1=The battery runtime is below configured minimum acceptable value
|  |  | 0 | 7 | Battery voltage does not match battery configuration | Battery voltage does not match battery configuration | TOO LONG | Battery voltage does not match battery configuration 1=Battery voltage does not match the battery configuration settings |  | 0 |  |  |  | BOOLEAN |  |  | 1=Battery voltage does not match the battery configuration settings
|  |  | 0 | 8 | Battery condition is weak | Battery condition is weak | TOO LONG | Battery condition is weak 1=Battery capacity is between 50% and 75% |  | 0 |  |  |  | BOOLEAN |  |  | 1=Battery capacity is between 50% and 75%
|  |  | 0 | 9 | Battery condition is poor | Battery condition is poor | TOO LONG | Battery condition is poor 1=Battery capacity is lower than 50% |  | 0 |  |  |  | BOOLEAN |  |  | 1=Battery capacity is lower than 50%
|  |  | 0 | 10 | High battery temperature level | High battery temperature level | TOO LONG | High battery temperature level 1=The battery temperature is above the alarm setting |  | 0 |  |  |  | BOOLEAN |  |  | 1=The battery temperature is above the alarm setting
|  |  | 0 | 11 | Low battery temperature level | Low battery temperature level | TOO LONG | Low battery temperature level 1=The battery temperature is below the alarm setting |  | 0 |  |  |  | BOOLEAN |  |  | 1=The battery temperature is below the alarm setting
|  |  | 0 | 12 | Battery capacity is below minimum acceptable level | Battery capacity is below minimum acceptable level | TOO LONG | Battery capacity is below minimum acceptable level 1=The battery capacity is below the minimum acceptable value according to UPS power rating. Risk of battery damage |  | 0 |  |  |  | BOOLEAN |  |  | 1=The battery capacity is below the minimum acceptable value according to UPS power rating. Risk of battery damage
|  |  | 0 | 13 | Battery charge power is reduced | Battery charge power is reduced | TOO LONG | Battery charge power is reduced 1=The battery charge power has been reduced |  | 0 |  |  |  | BOOLEAN |  |  | 1=The battery charge power has been reduced
|  |  | 0 | 14 | Battery is not working correctly | Battery is not working correctly | TOO LONG | Battery is not working correctly 1=A battery is not working correctly |  | 0 |  |  |  | BOOLEAN |  |  | 1=A battery is not working correctly
|  |  | 0 | 15 | Battery float charge current exceeds expected value | Battery float charge current exceeds expected value | TOO LONG | Battery float charge current exceeds expected value 1=The battery float charge current exceeds the expected value and has been limited to avoid thermal runaway |  | 0 |  |  |  | BOOLEAN |  |  | 1=The battery float charge current exceeds the expected value and has been limited to avoid thermal runaway
40005 | 0x0004 | 4 | 0 |  | Energy storage | Energy Storage 2 | 16 | Energy Storage 2 | Read Holding Registers | 0 | 40005 | Unsigned 16 bit Integer | 1 | BOOLEAN
|  |  | 0 | 0 | High battery temperature shutdown | High battery temperature shutdown | TOO LONG | High battery temperature shutdown 1=The energy storage surveillance has detected a battery temperature above shutdown limit |  | 0 |  |  |  | BOOLEAN |  |  | 1=The energy storage surveillance has detected a battery temperature above shutdown limit
|  |  | 0 | 1 | Battery configuration is incorrect | Battery configuration is incorrect | TOO LONG | Battery configuration is incorrect 1=The configuration of the settings for number of batteries in series, number of cells in battery and nominal cell voltage does not match the battery voltage range of the UPS |  | 0 |  |  |  | BOOLEAN |  |  | 1=The configuration of the settings for number of batteries in series, number of cells in battery and nominal cell voltage does not match the battery voltage range of the UPS
|  |  | 0 | 2 | Mixed battery brands on string level detected | Mixed battery brands on string level detected | TOO LONG | Mixed battery brands on string level detected 1=The battery modules in the string are not of the same brand |  | 0 |  |  |  | BOOLEAN |  |  | 1=The battery modules in the string are not of the same brand
|  |  | 0 | 3 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 4 | Mixed battery module commercial references on system level detected | Mixed battery module commercial references on system level detected | TOO LONG | Mixed battery module commercial references on system level detected 1=Mixed battery module commercial references on system level detected |  | 0 |  |  |  | BOOLEAN |  |  | 1=Mixed battery module commercial references on system level detected
|  |  | 0 | 5 | Modular battery breaker open | Modular battery breaker open | TOO LONG | Modular battery breaker open 1=Modular battery breaker is open |  | 0 |  |  |  | BOOLEAN |  |  | 1=Modular battery breaker is open
|  |  | 0 | 6 | Incorrect battery monitor controller (BMC) configuration detected | Incorrect battery monitor controller (BMC) configuration detected | TOO LONG | Incorrect battery monitor controller (BMC) configuration detected 1=Incorrect battery monitor controller (BMC) configuration detected |  | 0 |  |  |  | BOOLEAN |  |  | 1=Incorrect battery monitor controller (BMC) configuration detected
|  |  | 0 | 7 | Modular battery temperature out of tolerance | Modular battery temperature out of tolerance | TOO LONG | Modular battery temperature out of tolerance 1=Modular battery temperature is out of tolerance |  | 0 |  |  |  | BOOLEAN |  |  | 1=Modular battery temperature is out of tolerance
|  |  | 0 | 8 | Modular battery cabinet fuse blown | Modular battery cabinet fuse blown | TOO LONG | Modular battery cabinet fuse blown 1=Modular battery cabinet fuse blown |  | 0 |  |  |  | BOOLEAN |  |  | 1=Modular battery cabinet fuse blown
|  |  | 0 | 9 | Incomplete battery string detected | Incomplete battery string detected | TOO LONG | Incomplete battery string detected 1=Incomplete battery string detected |  | 0 |  |  |  | BOOLEAN |  |  | 1=Incomplete battery string detected
|  |  | 0 | 10 | Mixed battery solution detected | Mixed battery solution detected | TOO LONG | Mixed battery solution detected 1=The UPS is configured for a classic battery solution but one or more battery modules are detected present |  | 0 |  |  |  | BOOLEAN |  |  | 1=The UPS is configured for a classic battery solution but one or more battery modules are detected present
|  |  | 0 | 11 | Modular battery cabinet commercial reference unknown | Modular battery cabinet commercial reference unknown | TOO LONG | Modular battery cabinet commercial reference unknown 1=Modular battery cabinet commercial reference is unknown |  | 0 |  |  |  | BOOLEAN |  |  | 1=Modular battery cabinet commercial reference is unknown
|  |  | 0 | 12 | Battery module type unknown | Battery module type unknown | TOO LONG | Battery module type unknown 1=Battery module type is unknown |  | 0 |  |  |  | BOOLEAN |  |  | 1=Battery module type is unknown
|  |  | 0 | 13 | Battery module temperature sensor not working correctly | Battery module temperature sensor not working correctly | TOO LONG | Battery module temperature sensor not working correctly 1=Battery module temperature sensor is not working correctly |  | 0 |  |  |  | BOOLEAN |  |  | 1=Battery module temperature sensor is not working correctly
|  |  | 0 | 14 | Battery module temperature out of tolerance | Battery module temperature out of tolerance | TOO LONG | Battery module temperature out of tolerance 1=Battery module temperature is out of tolerance |  | 0 |  |  |  | BOOLEAN |  |  | 1=Battery module temperature is out of tolerance
|  |  | 0 | 15 | Modular battery DC relay open | Modular battery DC relay open | TOO LONG | Modular battery DC relay open 1=Modular battery DC relay open |  | 0 |  |  |  | BOOLEAN |  |  | 1=Modular battery DC relay open
40006 | 0x0005 | 5 | 0 |  | General | General 1 | 9 | General 1 | Read Holding Registers | 0 | 40006 | Unsigned 16 bit Integer | 1 | BOOLEAN
|  |  | 0 | 0 | EPO switch activated | EPO switch activated | TOO LONG | EPO switch activated 1=An emergency power off (EPO) switch is activated |  | 0 |  |  |  | BOOLEAN |  |  | 1=An emergency power off (EPO) switch is activated
|  |  | 0 | 1 | Synchronization unavailable - system is free running | Synchronization unavailable - system is free running | TOO LONG | Synchronization unavailable - system is free running 1=The UPS is unable to synchronize to the bypass input, external source or parallel system |  | 0 |  |  |  | BOOLEAN |  |  | 1=The UPS is unable to synchronize to the bypass input, external source or parallel system
|  |  | 0 | 2 | Inverter output is not in phase with bypass input | Inverter output is not in phase with bypass input | TOO LONG | Inverter output is not in phase with bypass input 1=The UPS inverter output is not in phase with the bypass input |  | 0 |  |  |  | BOOLEAN |  |  | 1=The UPS inverter output is not in phase with the bypass input
|  |  | 0 | 3 | UPS operation mode - Battery | UPS operation mode - Battery | TOO LONG | UPS operation mode - Battery 1=On battery power in response to an input power unavailability or due to a transfer out of ECOnversion |  | 0 |  |  |  | BOOLEAN |  |  | 1=On battery power in response to an input power unavailability or due to a transfer out of ECOnversion
|  |  | 0 | 4 | UPS operation mode - Requested static bypass | UPS operation mode - Requested static bypass | TOO LONG | UPS operation mode - Requested static bypass 1=The UPS is in bypass in response to a user-initiated command, typically for maintenance |  | 0 |  |  |  | BOOLEAN |  |  | 1=The UPS is in bypass in response to a user-initiated command, typically for maintenance
|  |  | 0 | 5 | UPS operation mode - Forced static bypass | UPS operation mode - Forced static bypass | TOO LONG | UPS operation mode - Forced static bypass 1=The UPS is in forced static bypass |  | 0 |  |  |  | BOOLEAN |  |  | 1=The UPS is in forced static bypass
|  |  | 0 | 6 | UPS operation mode - Maintenance bypass | UPS operation mode - Maintenance bypass | TOO LONG | UPS operation mode - Maintenance bypass 1=The UPS load is supplied through maintenance bypass breaker (MBB) |  | 0 |  |  |  | BOOLEAN |  |  | 1=The UPS load is supplied through maintenance bypass breaker (MBB)
|  |  | 0 | 7 | UPS operation mode - Battery test | UPS operation mode - Battery test | TOO LONG | UPS operation mode - Battery test 1=On battery power in response to a test of the performance of the batteries |  | 0 |  |  |  | BOOLEAN |  |  | 1=On battery power in response to a test of the performance of the batteries
|  |  | 0 | 8 | UPS operation mode - Off | UPS operation mode - Off | TOO LONG | UPS operation mode - Off 1=The output power is turned off |  | 0 |  |  |  | BOOLEAN |  |  | 1=The output power is turned off
|  |  | 0 | 9 | UPS operation mode - Initialization | UPS operation mode - Initialization | TOO LONG | UPS operation mode - Initialization 1=The UPS is initializing |  | 0 |  |  |  | BOOLEAN |  |  | 1=The UPS is initializing
|  |  | 0 | 10 | UPS operation mode - Static bypass standby | UPS operation mode - Static bypass standby | TOO LONG | UPS operation mode - Static bypass standby 1=The UPS is ready to enter static bypass but awaits permission from the system. UPS output is off |  | 0 |  |  |  | BOOLEAN |  |  | 1=The UPS is ready to enter static bypass but awaits permission from the system. UPS output is off
|  |  | 0 | 11 | UPS operation mode - Inverter standby | UPS operation mode - Inverter standby | TOO LONG | UPS operation mode - Inverter standby 1=The UPS is ready to enter battery operation but awaits permission from the system. UPS output is off |  | 0 |  |  |  | BOOLEAN |  |  | 1=The UPS is ready to enter battery operation but awaits permission from the system. UPS output is off
|  |  | 0 | 12 | System operation mode - Off | System operation mode - Off | TOO LONG | System operation mode - Off 1=The system output power is turned off |  | 0 |  |  |  | BOOLEAN |  |  | 1=The system output power is turned off
|  |  | 0 | 13 | System operation mode - Forced static bypass | System operation mode - Forced static bypass | TOO LONG | System operation mode - Forced static bypass 1=The system is in bypass in response to a critical event or an inverter off request |  | 0 |  |  |  | BOOLEAN |  |  | 1=The system is in bypass in response to a critical event or an inverter off request
|  |  | 0 | 14 | System operation mode - Requested static bypass | System operation mode - Requested static bypass | TOO LONG | System operation mode - Requested static bypass 1=The UPS is in bypass in response to a user-initiated command, typically for maintenance |  | 0 |  |  |  | BOOLEAN |  |  | 1=The UPS is in bypass in response to a user-initiated command, typically for maintenance
|  |  | 0 | 15 | System operation mode - Maintenance bypass | System operation mode - Maintenance bypass | TOO LONG | System operation mode - Maintenance bypass 1=The system load is supplied through maintenance bypass breaker (MBB) |  | 0 |  |  |  | BOOLEAN |  |  | 1=The system load is supplied through maintenance bypass breaker (MBB)
40007 | 0x0006 | 6 | 0 |  | General | General 2 | 9 | General 2 | Read Holding Registers | 0 | 40007 | Unsigned 16 bit Integer | 1 | BOOLEAN
|  |  | 0 | 0 | System operation mode - Static bypass standby | System operation mode - Static bypass standby | TOO LONG | System operation mode - Static bypass standby 1=The system is in static bypass standby operation in response to a critical event or an inverter off request |  | 0 |  |  |  | BOOLEAN |  |  | 1=The system is in static bypass standby operation in response to a critical event or an inverter off request
|  |  | 0 | 1 | Product not registered | Product not registered | TOO LONG | Product not registered 1=Your UPS is not registered |  | 0 |  |  |  | BOOLEAN |  |  | 1=Your UPS is not registered
|  |  | 0 | 2 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 3 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 4 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 5 | Activation code is not valid for UPS | Activation code is not valid for UPS | TOO LONG | Activation code is not valid for UPS 1=The activation code is not valid for UPS |  | 0 |  |  |  | BOOLEAN |  |  | 1=The activation code is not valid for UPS
|  |  | 0 | 6 | Activation code missing | Activation code missing | TOO LONG | Activation code missing 1=The activation code is missing |  | 0 |  |  |  | BOOLEAN |  |  | 1=The activation code is missing
|  |  | 0 | 7 | RFID tag has changed | RFID tag has changed | TOO LONG | RFID tag has changed 1=The RFID tag has changed |  | 0 |  |  |  | BOOLEAN |  |  | 1=The RFID tag has changed
|  |  | 0 | 8 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 9 | System locked in bypass operation | System locked in bypass operation | TOO LONG | System locked in bypass operation 1=The system is locked in bypass operation |  | 0 |  |  |  | BOOLEAN |  |  | 1=The system is locked in bypass operation
|  |  | 0 | 10 | Unsupported power frame type detected | Unsupported power frame type detected | TOO LONG | Unsupported power frame type detected 1=The detected UPS power frame type is not supported by the current UPS power configuration |  | 0 |  |  |  | BOOLEAN |  |  | 1=The detected UPS power frame type is not supported by the current UPS power configuration
|  |  | 0 | 11 | Unsupported power module type detected | Unsupported power module type detected | TOO LONG | Unsupported power module type detected 1=The detected power module type is not supported by the current UPS power configuration |  | 0 |  |  |  | BOOLEAN |  |  | 1=The detected power module type is not supported by the current UPS power configuration
|  |  | 0 | 12 | Unsupported static bypass switch module type detected | Unsupported static bypass switch module type detected | TOO LONG | Unsupported static bypass switch module type detected 1=The detected static bypass switch module type is not supported by the current UPS power configuration |  | 0 |  |  |  | BOOLEAN |  |  | 1=The detected static bypass switch module type is not supported by the current UPS power configuration
|  |  | 0 | 13 | Incorrect system voltage configuration detected | Incorrect system voltage configuration detected | TOO LONG | Incorrect system voltage configuration detected 1=The configured UPS system voltage is not within the allowed range |  | 0 |  |  |  | BOOLEAN |  |  | 1=The configured UPS system voltage is not within the allowed range
|  |  | 0 | 14 | Configured UPS power rating exceeds frame power rating | Configured UPS power rating exceeds frame power rating | TOO LONG | Configured UPS power rating exceeds frame power rating 1=The configured UPS power rating is larger than the power rating of the frame |  | 0 |  |  |  | BOOLEAN |  |  | 1=The configured UPS power rating is larger than the power rating of the frame
|  |  | 0 | 15 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
40008 | 0x0007 | 7 | 0 |  | General | General 3 | 9 | General 3 | Read Holding Registers | 0 | 40008 | Unsigned 16 bit Integer | 1 | BOOLEAN
|  |  | 0 | 0 | Incorrect 3-wire configuration detected | Incorrect 3-wire configuration detected | TOO LONG | Incorrect 3-wire configuration detected 1=The UPS is not allowed to operate as a 3-wire system at the configured UPS system voltage |  | 0 |  |  |  | BOOLEAN |  |  | 1=The UPS is not allowed to operate as a 3-wire system at the configured UPS system voltage
|  |  | 0 | 1 | No static bypass switch present | No static bypass switch present | TOO LONG | No static bypass switch present 1=No static bypass switch detected present |  | 0 |  |  |  | BOOLEAN |  |  | 1=No static bypass switch detected present
|  |  | 0 | 2 | No power module(s) present | No power module(s) present | TOO LONG | No power module(s) present 1=No power module(s) detected present |  | 0 |  |  |  | BOOLEAN |  |  | 1=No power module(s) detected present
|  |  | 0 | 3 | Available UPS power lower than configured UPS power rating | Available UPS power lower than configured UPS power rating | TOO LONG | Available UPS power lower than configured UPS power rating 1=The available UPS power from inverter is lower than the configured UPS power rating |  | 0 |  |  |  | BOOLEAN |  |  | 1=The available UPS power from inverter is lower than the configured UPS power rating
|  |  | 0 | 4 | Static bypass switch power rating lower than configured UPS power rating | Static bypass switch power rating lower than configured UPS power rating | TOO LONG | Static bypass switch power rating lower than configured UPS power rating 1=The static bypass switch power rating is lower than the configured UPS power rating. UPS power rating has been derated to match static bypass switch power rating |  | 0 |  |  |  | BOOLEAN |  |  | 1=The static bypass switch power rating is lower than the configured UPS power rating. UPS power rating has been derated to match static bypass switch power rating
|  |  | 0 | 5 | Ambient temperature out of tolerance | Ambient temperature out of tolerance | TOO LONG | Ambient temperature out of tolerance 1=The ambient temperature out of tolerance |  | 0 |  |  |  | BOOLEAN |  |  | 1=The ambient temperature out of tolerance
|  |  | 0 | 6 | Ambient temperature high | Ambient temperature high | TOO LONG | Ambient temperature high 1=Ambient temperature is high |  | 0 |  |  |  | BOOLEAN |  |  | 1=Ambient temperature is high
|  |  | 0 | 7 | Inverter is off due to a request by the user | Inverter is off due to a request by the user | TOO LONG | Inverter is off due to a request by the user 1=The inverter is off due to a request by the user |  | 0 |  |  |  | BOOLEAN |  |  | 1=The inverter is off due to a request by the user
|  |  | 0 | 8 | Settings file not accepted | Settings file not accepted | TOO LONG | Settings file not accepted 1=The settings file is not valid or not intended for this UPS |  | 0 |  |  |  | BOOLEAN |  |  | 1=The settings file is not valid or not intended for this UPS
|  |  | 0 | 9 | Warranty expiring soon | Warranty expiring soon | TOO LONG | Warranty expiring soon 1=The product is reaching the end of warranty |  | 0 |  |  |  | BOOLEAN |  |  | 1=The product is reaching the end of warranty
|  |  | 0 | 10 | Technical check recommended | Technical check recommended | TOO LONG | Technical check recommended 1=The product and its batteries need to be checked as preventive maintenance is recommended |  | 0 |  |  |  | BOOLEAN |  |  | 1=The product and its batteries need to be checked as preventive maintenance is recommended
|  |  | 0 | 11 | Air filter technical check recommended | Air filter technical check recommended | TOO LONG | Air filter technical check recommended 1=The air filters need to be checked as preventive maintenance is recommended |  | 0 |  |  |  | BOOLEAN |  |  | 1=The air filters need to be checked as preventive maintenance is recommended
|  |  | 0 | 12 | Controller box disabled | Controller box disabled | TOO LONG | Controller box disabled 1=Controller box has been disabled by user |  | 0 |  |  |  | BOOLEAN |  |  | 1=Controller box has been disabled by user
|  |  | 0 | 13 | UPS surveillance detected fault | UPS surveillance detected fault | TOO LONG | UPS surveillance detected fault 1=UPS surveillance detected a fault |  | 0 |  |  |  | BOOLEAN |  |  | 1=UPS surveillance detected a fault
|  |  | 0 | 14 | Display communication lost - display is disconnected from the system | Display communication lost - display is disconnected from the system | TOO LONG | Display communication lost - display is disconnected from the system 1=Communication link between display and SLC is lost. Display is disconnected from the system |  | 0 |  |  |  | BOOLEAN |  |  | 1=Communication link between display and SLC is lost. Display is disconnected from the system
|  |  | 0 | 15 | Display communication lost but the display is connected to the system | Display communication lost but the display is connected to the system | TOO LONG | Display communication lost but the display is connected to the system 1=Communication link between display and SLC is lost but the display is connected to the system |  | 0 |  |  |  | BOOLEAN |  |  | 1=Communication link between display and SLC is lost but the display is connected to the system
40009 | 0x0008 | 8 | 0 |  | General | General 4 | 9 | General 4 | Read Holding Registers | 0 | 40009 | Unsigned 16 bit Integer | 1 | BOOLEAN
|  |  | 0 | 0 | Display communication not authenticated | Display communication not authenticated | TOO LONG | Display communication not authenticated 1=Communication link between display and SLC is not authenticated |  | 0 |  |  |  | BOOLEAN |  |  | 1=Communication link between display and SLC is not authenticated
|  |  | 0 | 1 | Multiple NTP server connections enabled | Multiple NTP server connections enabled | TOO LONG | Multiple NTP server connections enabled 1=Multiple NTP server connections are enabled |  | 0 |  |  |  | BOOLEAN |  |  | 1=Multiple NTP server connections are enabled
|  |  | 0 | 2 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 3 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 4 | Incorrect UPS model number detected | Incorrect UPS model number detected | TOO LONG | Incorrect UPS model number detected 1=The UPS model number does not match the UPS base model number |  | 0 |  |  |  | BOOLEAN |  |  | 1=The UPS model number does not match the UPS base model number
|  |  | 0 | 5 | Incorrect UPS base model number detected | Incorrect UPS base model number detected | TOO LONG | Incorrect UPS base model number detected 1=The UPS base model number does not match the installed frame type, power module type, and/or SBS type |  | 0 |  |  |  | BOOLEAN |  |  | 1=The UPS base model number does not match the installed frame type, power module type, and/or SBS type
|  |  | 0 | 6 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 7 | Internal power module redundancy lost | Internal power module redundancy lost | TOO LONG | Internal power module redundancy lost 1=The configured internal power module redundancy is lost because there are not enough power modules available |  | 0 |  |  |  | BOOLEAN |  |  | 1=The configured internal power module redundancy is lost because there are not enough power modules available
|  |  | 0 | 8 | UPS output load is too low to allow ECOnversion | UPS output load is too low to allow ECOnversion | TOO LONG | UPS output load is too low to allow ECOnversion 1=UPS output load is too low to allow ECOnversion |  | 0 |  |  |  | BOOLEAN |  |  | 1=UPS output load is too low to allow ECOnversion
|  |  | 0 | 9 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 10 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 11 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 12 | UPS output load power factor is too low to allow ECOnversion | UPS output load power factor is too low to allow ECOnversion | TOO LONG | UPS output load power factor is too low to allow ECOnversion 1=UPS output load power factor is too low to allow ECOnversion |  | 0 |  |  |  | BOOLEAN |  |  | 1=UPS output load power factor is too low to allow ECOnversion
|  |  | 0 | 13 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 14 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 15 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
40010 | 0x0009 | 9 | 0 |  | RESERVED | Reserved 1 | 10 | Reserved 1 | Read Holding Registers | 0 | 40010 | Unsigned 16 bit Integer | 1 | BOOLEAN
40011 | 0x000A | 10 | 0 |  | RESERVED | Reserved 2 | 10 | Reserved 2 | Read Holding Registers | 0 | 40011 | Unsigned 16 bit Integer | 1 | BOOLEAN
40012 | 0x000B | 11 | 0 |  | Input | Input | 5 | Input | Read Holding Registers | 0 | 40012 | Unsigned 16 bit Integer | 1 | BOOLEAN
|  |  | 0 | 0 | Input voltage out of tolerance | Input voltage out of tolerance | TOO LONG | Input voltage out of tolerance 1=Input voltage is out of tolerance |  | 0 |  |  |  | BOOLEAN |  |  | 1=Input voltage is out of tolerance
|  |  | 0 | 1 | Input phase sequence incorrect | Input phase sequence incorrect | TOO LONG | Input phase sequence incorrect 1=The phase rotation on input is incorrect |  | 0 |  |  |  | BOOLEAN |  |  | 1=The phase rotation on input is incorrect
|  |  | 0 | 2 | Input frequency out of tolerance | Input frequency out of tolerance | TOO LONG | Input frequency out of tolerance 1=Input frequency is out of tolerance |  | 0 |  |  |  | BOOLEAN |  |  | 1=Input frequency is out of tolerance
|  |  | 0 | 3 | Input phase missing | Input phase missing | TOO LONG | Input phase missing 1=Input is missing a phase |  | 0 |  |  |  | BOOLEAN |  |  | 1=Input is missing a phase
|  |  | 0 | 4 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 5 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 6 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 7 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 8 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 9 | Neutral displacement detected | Neutral displacement detected | TOO LONG | Neutral displacement detected 1=Neutral displacement detected |  | 0 |  |  |  | BOOLEAN |  |  | 1=Neutral displacement detected
|  |  | 0 | 10 | Bonding between neutral and ground missing | Bonding between neutral and ground missing | TOO LONG | Bonding between neutral and ground missing 1=Bonding between neutral and ground is missing |  | 0 |  |  |  | BOOLEAN |  |  | 1=Bonding between neutral and ground is missing
|  |  | 0 | 11 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 12 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 13 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 14 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 15 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
40013 | 0x000C | 12 | 0 |  | Output | Output | 6 | Output | Read Holding Registers | 0 | 40013 | Unsigned 16 bit Integer | 1 | BOOLEAN
|  |  | 0 | 0 | Output voltage out of tolerance | Output voltage out of tolerance | TOO LONG | Output voltage out of tolerance 1=The output voltage is out of tolerance |  | 0 |  |  |  | BOOLEAN |  |  | 1=The output voltage is out of tolerance
|  |  | 0 | 1 | Output frequency out of tolerance | Output frequency out of tolerance | TOO LONG | Output frequency out of tolerance 1=The output frequency is out of tolerance |  | 0 |  |  |  | BOOLEAN |  |  | 1=The output frequency is out of tolerance
|  |  | 0 | 2 | Overload or short-circuit on UPS | Overload or short-circuit on UPS | TOO LONG | Overload or short-circuit on UPS 1=The load exceeds 100% of rated capacity or there is a short-circuit on the output |  | 0 |  |  |  | BOOLEAN |  |  | 1=The load exceeds 100% of rated capacity or there is a short-circuit on the output
|  |  | 0 | 3 | Overload on UPS due to high ambient temperature | Overload on UPS due to high ambient temperature | TOO LONG | Overload on UPS due to high ambient temperature 1=The load exceeds the rated UPS capacity when running in high ambient temperature |  | 0 |  |  |  | BOOLEAN |  |  | 1=The load exceeds the rated UPS capacity when running in high ambient temperature
|  |  | 0 | 4 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 5 | Load on UPS is above warning level | Load on UPS is above warning level | TOO LONG | Load on UPS is above warning level 1=Load on UPS has exceeded the warning level |  | 0 |  |  |  | BOOLEAN |  |  | 1=Load on UPS has exceeded the warning level
|  |  | 0 | 6 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 7 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 8 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 9 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 10 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 11 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 12 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 13 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 14 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 15 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
40014 | 0x000D | 13 | 0 |  | Parallel system | Parallel system | 15 | Parallel system | Read Holding Registers | 0 | 40014 | Unsigned 16 bit Integer | 1 | BOOLEAN
|  |  | 0 | 0 | Parallel communication lost on PBUS cable 1 | Parallel communication lost on PBUS cable 1 | TOO LONG | Parallel communication lost on PBUS cable 1 1=PBUS cable 1 may be damaged |  | 0 |  |  |  | BOOLEAN |  |  | 1=PBUS cable 1 may be damaged
|  |  | 0 | 1 | Parallel communication lost on PBUS cable 2 | Parallel communication lost on PBUS cable 2 | TOO LONG | Parallel communication lost on PBUS cable 2 1=PBUS cable 2 may be damaged |  | 0 |  |  |  | BOOLEAN |  |  | 1=PBUS cable 2 may be damaged
|  |  | 0 | 2 | General parallel system event | General parallel system event | TOO LONG | General parallel system event 1=The parallel system is not configured correctly or is not working correctly |  | 0 |  |  |  | BOOLEAN |  |  | 1=The parallel system is not configured correctly or is not working correctly
|  |  | 0 | 3 | Parallel mixed operation mode | Parallel mixed operation mode | TOO LONG | Parallel mixed operation mode 1=One or more parallel UPSs are operating in battery operation, while others are operating in normal operation |  | 0 |  |  |  | BOOLEAN |  |  | 1=One or more parallel UPSs are operating in battery operation, while others are operating in normal operation
|  |  | 0 | 4 | Parallel unit not present | Parallel unit not present | TOO LONG | Parallel unit not present 1=UPS is unable to communicate with one of the parallel UPSs. The UPS might have been powered down or PBUS cables may be damaged |  | 0 |  |  |  | BOOLEAN |  |  | 1=UPS is unable to communicate with one of the parallel UPSs. The UPS might have been powered down or PBUS cables may be damaged
|  |  | 0 | 5 | Parallel redundancy lost | Parallel redundancy lost | TOO LONG | Parallel redundancy lost 1=The configured parallel redundancy is lost, either because the output load is too high, or because there are not enough parallel UPSs available. |  | 0 |  |  |  | BOOLEAN |  |  | 1=The configured parallel redundancy is lost, either because the output load is too high, or because there are not enough parallel UPSs available.
|  |  | 0 | 6 | Not enough UPSs ready to turn on inverter | Not enough UPSs ready to turn on inverter | TOO LONG | Not enough UPSs ready to turn on inverter 1=One or more parallel UPSs have been requested to turn on inverter, but not enough UPSs are ready for system to enter inverter on operation |  | 0 |  |  |  | BOOLEAN |  |  | 1=One or more parallel UPSs have been requested to turn on inverter, but not enough UPSs are ready for system to enter inverter on operation
|  |  | 0 | 7 | Firmware versions in parallel UPSs are not identical | Firmware versions in parallel UPSs are not identical | TOO LONG | Firmware versions in parallel UPSs are not identical 1=The firmware versions in parallel UPSs are not identical |  | 0 |  |  |  | BOOLEAN |  |  | 1=The firmware versions in parallel UPSs are not identical
|  |  | 0 | 8 | Confirm redundancy lost and/or transfer to forced static bypass | Confirm redundancy lost and/or transfer to forced static bypass | TOO LONG | Confirm redundancy lost and/or transfer to forced static bypass 1=Inverter OFF button has been pushed and user must confirm that the redundancy will be lost and/or system will transfer to forced static bypass |  | 0 |  |  |  | BOOLEAN |  |  | 1=Inverter OFF button has been pushed and user must confirm that the redundancy will be lost and/or system will transfer to forced static bypass
|  |  | 0 | 9 | IMB closed in parallel system with MBB | IMB closed in parallel system with MBB | TOO LONG | IMB closed in parallel system with MBB 1=IMB has been closed in parallel system with MBB |  | 0 |  |  |  | BOOLEAN |  |  | 1=IMB has been closed in parallel system with MBB
|  |  | 0 | 10 | Parallel breaker status inconsistency detected | Parallel breaker status inconsistency detected | TOO LONG | Parallel breaker status inconsistency detected 1=The status of one or more common parallel breakers is not detected to be the same on all parallel UPS |  | 0 |  |  |  | BOOLEAN |  |  | 1=The status of one or more common parallel breakers is not detected to be the same on all parallel UPS
|  |  | 0 | 11 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 12 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 13 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 14 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 15 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
40015 | 0x000E | 14 | 0 |  | Power module | Power module | 12 | Power module | Read Holding Registers | 0 | 40015 | Unsigned 16 bit Integer | 1 | BOOLEAN
|  |  | 0 | 0 | Power module inoperable | Power module inoperable | TOO LONG | Power module inoperable 1=Power module is inoperable |  | 0 |  |  |  | BOOLEAN |  |  | 1=Power module is inoperable
|  |  | 0 | 1 | Power module temperature warning | Power module temperature warning | TOO LONG | Power module temperature warning 1=Power module temperature exceeds warning level |  | 0 |  |  |  | BOOLEAN |  |  | 1=Power module temperature exceeds warning level
|  |  | 0 | 2 | Power module overheated | Power module overheated | TOO LONG | Power module overheated 1=Power module temperature exceeds critical level |  | 0 |  |  |  | BOOLEAN |  |  | 1=Power module temperature exceeds critical level
|  |  | 0 | 3 | Power module inlet temperature high | Power module inlet temperature high | TOO LONG | Power module inlet temperature high 1=The power module inlet temperature is high |  | 0 |  |  |  | BOOLEAN |  |  | 1=The power module inlet temperature is high
|  |  | 0 | 4 | Power module inlet temperature out of tolerance | Power module inlet temperature out of tolerance | TOO LONG | Power module inlet temperature out of tolerance 1=The power module inlet temperature is out of tolerance |  | 0 |  |  |  | BOOLEAN |  |  | 1=The power module inlet temperature is out of tolerance
|  |  | 0 | 5 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 6 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 7 | Power module fan inoperable | Power module fan inoperable | TOO LONG | Power module fan inoperable 1=The power module has one or more inoperable fans. Fan redundancy is lost |  | 0 |  |  |  | BOOLEAN |  |  | 1=The power module has one or more inoperable fans. Fan redundancy is lost
|  |  | 0 | 8 | Power module disabled | Power module disabled | TOO LONG | Power module disabled 1=The power module has been disabled |  | 0 |  |  |  | BOOLEAN |  |  | 1=The power module has been disabled
|  |  | 0 | 9 | Power module surveillance detected fault | Power module surveillance detected fault | TOO LONG | Power module surveillance detected fault 1=Power module surveillance detected a fault |  | 0 |  |  |  | BOOLEAN |  |  | 1=Power module surveillance detected a fault
|  |  | 0 | 10 | PMC communication lost - disconnected | PMC communication lost - disconnected | TOO LONG | PMC communication lost - disconnected 1=Communication link between PMC and UC is lost. PMC is disconnected |  | 0 |  |  |  | BOOLEAN |  |  | 1=Communication link between PMC and UC is lost. PMC is disconnected
|  |  | 0 | 11 | PMC communication lost - connected | PMC communication lost - connected | TOO LONG | PMC communication lost - connected 1=Communication link between PMC and UC is lost. PMC is connected |  | 0 |  |  |  | BOOLEAN |  |  | 1=Communication link between PMC and UC is lost. PMC is connected
|  |  | 0 | 12 | PMC communication not authenticated | PMC communication not authenticated | TOO LONG | PMC communication not authenticated 1=Communication link between PMC and UC is not authenticated |  | 0 |  |  |  | BOOLEAN |  |  | 1=Communication link between PMC and UC is not authenticated
|  |  | 0 | 13 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 14 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 15 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
40016 | 0x000F | 15 | 0 |  | RESERVED | Reserved 3 | 10 | Reserved 3 | Read Holding Registers | 0 | 40016 | Unsigned 16 bit Integer | 1 | BOOLEAN
40017 | 0x0010 | 16 | 0 |  | Static bypass switch | Static bypass switch | 20 | Static bypass switch | Read Holding Registers | 0 | 40017 | Unsigned 16 bit Integer | 1 | BOOLEAN
|  |  | 0 | 0 | Static bypass switch fan inoperable | Static bypass switch fan inoperable | TOO LONG | Static bypass switch fan inoperable 1=Static bypass switch has one or more inoperable fans. Fan redundancy is lost |  | 0 |  |  |  | BOOLEAN |  |  | 1=Static bypass switch has one or more inoperable fans. Fan redundancy is lost
|  |  | 0 | 1 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 2 | Static bypass switch warning | Static bypass switch warning | TOO LONG | Static bypass switch warning 1=The static bypass switch needs a technical check but is still fully operational |  | 0 |  |  |  | BOOLEAN |  |  | 1=The static bypass switch needs a technical check but is still fully operational
|  |  | 0 | 3 | Static bypass switch inoperable | Static bypass switch inoperable | TOO LONG | Static bypass switch inoperable 1=Static bypass switch is inoperable. UPS is prevented from going into static bypass operation |  | 0 |  |  |  | BOOLEAN |  |  | 1=Static bypass switch is inoperable. UPS is prevented from going into static bypass operation
|  |  | 0 | 4 | Static bypass switch controller communication lost -disconnected | Static bypass switch controller communication lost -disconnected | TOO LONG | Static bypass switch controller communication lost -disconnected 1=Communication link between static bypass switch controller and unit controller is lost. Static bypass switch controller is disconnected |  | 0 |  |  |  | BOOLEAN |  |  | 1=Communication link between static bypass switch controller and unit controller is lost. Static bypass switch controller is disconnected
|  |  | 0 | 5 | Static bypass switch controller communication lost -connected | Static bypass switch controller communication lost -connected | TOO LONG | Static bypass switch controller communication lost -connected 1=Communication link between static bypass switch controller and unit controller is lost. Static bypass switch controller is connected |  | 0 |  |  |  | BOOLEAN |  |  | 1=Communication link between static bypass switch controller and unit controller is lost. Static bypass switch controller is connected
|  |  | 0 | 6 | Static bypass switch controller communication not authenticated | Static bypass switch controller communication not authenticated | TOO LONG | Static bypass switch controller communication not authenticated 1=Communication link between static bypass switch controller and unit controller is not authenticated |  | 0 |  |  |  | BOOLEAN |  |  | 1=Communication link between static bypass switch controller and unit controller is not authenticated
|  |  | 0 | 7 | Static bypass switch module disabled | Static bypass switch module disabled | TOO LONG | Static bypass switch module disabled 1=The static bypass switch module has been disabled by user |  | 0 |  |  |  | BOOLEAN |  |  | 1=The static bypass switch module has been disabled by user
|  |  | 0 | 8 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 9 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 10 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 11 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 12 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 13 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 14 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 15 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
40018 | 0x0011 | 17 | 0 |  | Switchgear | Switchgear 1 | 12 | Switchgear 1 | Read Holding Registers | 0 | 40018 | Unsigned 16 bit Integer | 1 | BOOLEAN
|  |  | 0 | 0 | Breaker UIB open | Breaker UIB open | TOO LONG | Breaker UIB open 1=Unit input breaker UIB is open, and the UPS is prevented from running in normal operation |  | 0 |  |  |  | BOOLEAN |  |  | 1=Unit input breaker UIB is open, and the UPS is prevented from running in normal operation
|  |  | 0 | 1 | Breaker UOB open | Breaker UOB open | TOO LONG | Breaker UOB open 1=Unit output breaker UOB is open, and the UPS is prevented from supplying the load |  | 0 |  |  |  | BOOLEAN |  |  | 1=Unit output breaker UOB is open, and the UPS is prevented from supplying the load
|  |  | 0 | 2 | Breaker MBB closed | Breaker MBB closed | TOO LONG | Breaker MBB closed 1=Maintenance bypass breaker MBB is closed, supplying the load with unprotected power from bypass |  | 0 |  |  |  | BOOLEAN |  |  | 1=Maintenance bypass breaker MBB is closed, supplying the load with unprotected power from bypass
|  |  | 0 | 3 | Breaker SIB open | Breaker SIB open | TOO LONG | Breaker SIB open 1=System isolation breaker SIB is open, and system cannot supply the load |  | 0 |  |  |  | BOOLEAN |  |  | 1=System isolation breaker SIB is open, and system cannot supply the load
|  |  | 0 | 4 | Breaker SSIB open | Breaker SSIB open | TOO LONG | Breaker SSIB open 1=Static switch input breaker SSIB is open, preventing static bypass operation |  | 0 |  |  |  | BOOLEAN |  |  | 1=Static switch input breaker SSIB is open, preventing static bypass operation
|  |  | 0 | 5 | Breaker IMB closed | Breaker IMB closed | TOO LONG | Breaker IMB closed 1=Internal maintenance bypass breaker IMB is closed, supplying the load with unprotected power from bypass |  | 0 |  |  |  | BOOLEAN |  |  | 1=Internal maintenance bypass breaker IMB is closed, supplying the load with unprotected power from bypass
|  |  | 0 | 6 | Breaker RIMB closed | Breaker RIMB closed | TOO LONG | Breaker RIMB closed 1=Remote internal maintenance bypass breaker RIMB is closed, supplying the load with unprotected power from bypass |  | 0 |  |  |  | BOOLEAN |  |  | 1=Remote internal maintenance bypass breaker RIMB is closed, supplying the load with unprotected power from bypass
|  |  | 0 | 7 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 8 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 9 | Ground fault detected | Ground fault detected | TOO LONG | Ground fault detected 1=Dry contact input indicates that a ground wire fault has been detected |  | 0 |  |  |  | BOOLEAN |  |  | 1=Dry contact input indicates that a ground wire fault has been detected
|  |  | 0 | 10 | Genset is supplying the UPS | Genset is supplying the UPS | TOO LONG | Genset is supplying the UPS 1=Dry contact input indicates that a genset is supplying the UPS |  | 0 |  |  |  | BOOLEAN |  |  | 1=Dry contact input indicates that a genset is supplying the UPS
|  |  | 0 | 11 | Battery room ventilation inoperable | Battery room ventilation inoperable | TOO LONG | Battery room ventilation inoperable 1=Dry contact input indicates that the battery room ventilation is not working correctly |  | 0 |  |  |  | BOOLEAN |  |  | 1=Dry contact input indicates that the battery room ventilation is not working correctly
|  |  | 0 | 12 | External battery monitoring detected fault | External battery monitoring detected fault | TOO LONG | External battery monitoring detected fault 1=Dry contact input indicates external battery monitoring detected fault |  | 0 |  |  |  | BOOLEAN |  |  | 1=Dry contact input indicates external battery monitoring detected fault
|  |  | 0 | 13 | UOB redundant monitoring not working correctly | UOB redundant monitoring not working correctly | TOO LONG | UOB redundant monitoring not working correctly 1=The two redundant AUX contacts of UOB do not report the same status |  | 0 |  |  |  | BOOLEAN |  |  | 1=The two redundant AUX contacts of UOB do not report the same status
|  |  | 0 | 14 | MBB redundant monitoring not working correctly | MBB redundant monitoring not working correctly | TOO LONG | MBB redundant monitoring not working correctly 1=The two redundant AUX contacts of MBB do not report the same status |  | 0 |  |  |  | BOOLEAN |  |  | 1=The two redundant AUX contacts of MBB do not report the same status
|  |  | 0 | 15 | IMB redundant monitoring not working correctly | IMB redundant monitoring not working correctly | TOO LONG | IMB redundant monitoring not working correctly 1=The two redundant AUX contacts of IMB do not report the same status |  | 0 |  |  |  | BOOLEAN |  |  | 1=The two redundant AUX contacts of IMB do not report the same status
40019 | 0x0012 | 18 | 0 |  | Switchgear | Switchgear 2 | 12 | Switchgear 2 | Read Holding Registers | 0 | 40019 | Unsigned 16 bit Integer | 1 | BOOLEAN
|  |  | 0 | 0 | RIMB redundant monitoring not working correctly | RIMB redundant monitoring not working correctly | TOO LONG | RIMB redundant monitoring not working correctly 1=The two redundant AUX contacts of RIMB do not report the same status |  | 0 |  |  |  | BOOLEAN |  |  | 1=The two redundant AUX contacts of RIMB do not report the same status
|  |  | 0 | 1 | UPS locked in static bypass mode: activated | UPS locked in static bypass mode: activated | TOO LONG | UPS locked in static bypass mode: activated 1=Dry contact input for UPS locked in static bypass mode is activated |  | 0 |  |  |  | BOOLEAN |  |  | 1=Dry contact input for UPS locked in static bypass mode is activated
|  |  | 0 | 2 | High efficiency mode disabled | High efficiency mode disabled | TOO LONG | High efficiency mode disabled 1=High efficiency mode is disabled from a dry contact input |  | 0 |  |  |  | BOOLEAN |  |  | 1=High efficiency mode is disabled from a dry contact input
|  |  | 0 | 3 | External energy storage monitoring: minor alarm | External energy storage monitoring: minor alarm | TOO LONG | External energy storage monitoring: minor alarm 1=Dry contact input indicates external energy storage monitoring has detected a minor fault |  | 0 |  |  |  | BOOLEAN |  |  | 1=Dry contact input indicates external energy storage monitoring has detected a minor fault
|  |  | 0 | 4 | External energy storage monitoring: major alarm | External energy storage monitoring: major alarm | TOO LONG | External energy storage monitoring: major alarm 1=Dry contact input indicates external energy storage monitoring has detected a major fault |  | 0 |  |  |  | BOOLEAN |  |  | 1=Dry contact input indicates external energy storage monitoring has detected a major fault
|  |  | 0 | 5 | External charger off command: activated | External charger off command: activated | TOO LONG | External charger off command: activated 1=Dry contact input for charger off is activated |  | 0 |  |  |  | BOOLEAN |  |  | 1=Dry contact input for charger off is activated
|  |  | 0 | 6 | Temperature of input and/or output transformer is too high | Temperature of input and/or output transformer is too high | TOO LONG | Temperature of input and/or output transformer is too high 1=Temperature of input and/or output transformer is too high |  | 0 |  |  |  | BOOLEAN |  |  | 1=Temperature of input and/or output transformer is too high
|  |  | 0 | 7 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 8 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 9 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 10 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 11 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 12 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 13 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 14 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 15 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
40020 | 0x0013 | 19 | 0 |  | System level controller (SLC) | System level controller - SLC | 29 | System level controller - SLC | Read Holding Registers | 0 | 40020 | Unsigned 16 bit Integer | 1 | BOOLEAN
|  |  | 0 | 0 | SLC in controller box is not working correctly | SLC in controller box is not working correctly | TOO LONG | SLC in controller box is not working correctly 1=The SLC in the controller box is not working correctly |  | 0 |  |  |  | BOOLEAN |  |  | 1=The SLC in the controller box is not working correctly
|  |  | 0 | 1 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 2 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 3 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 4 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 5 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 6 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 7 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 8 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 9 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 10 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 11 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 12 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 13 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 14 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 15 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
40021 | 0x0014 | 20 | 0 |  | Unit controller (UC) | Unit Controller - UC | 20 | Unit Controller - UC | Read Holding Registers | 0 | 40021 | Unsigned 16 bit Integer | 1 | BOOLEAN
|  |  | 0 | 0 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 1 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 2 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 3 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 4 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 5 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 6 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 7 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 8 | UC in controller box is not working correctly | UC in controller box is not working correctly | TOO LONG | UC in controller box is not working correctly 1=The UC in the controller box is not working correctly |  | 0 |  |  |  | BOOLEAN |  |  | 1=The UC in the controller box is not working correctly
|  |  | 0 | 9 | UC communication lost - disconnected | UC communication lost - disconnected | TOO LONG | UC communication lost - disconnected 1=Communication link between UC and SLC is lost. UC is disconnected |  | 0 |  |  |  | BOOLEAN |  |  | 1=Communication link between UC and SLC is lost. UC is disconnected
|  |  | 0 | 10 | UC communication lost - connected | UC communication lost - connected | TOO LONG | UC communication lost - connected 1=Communication link between UC and SLC is lost. UC is connected |  | 0 |  |  |  | BOOLEAN |  |  | 1=Communication link between UC and SLC is lost. UC is connected
|  |  | 0 | 11 | UC communication not authenticated | UC communication not authenticated | TOO LONG | UC communication not authenticated 1=Communication link between UC and SLC is not authenticated |  | 0 |  |  |  | BOOLEAN |  |  | 1=Communication link between UC and SLC is not authenticated
|  |  | 0 | 12 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 13 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 14 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 15 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
40022 | 0x0015 | 21 | 0 |  | Battery Charger | Battery Charger | 15 | Battery Charger | Read Holding Registers | 0 | 40022 | Unsigned 16 bit Integer | 1 | BOOLEAN
|  |  | 0 | 0 | BMC communication lost - disconnected | BMC communication lost - disconnected | TOO LONG | BMC communication lost - disconnected 1=Communication link between BMC and SLC is lost. BMC is disconnected |  | 0 |  |  |  | BOOLEAN |  |  | 1=Communication link between BMC and SLC is lost. BMC is disconnected
|  |  | 0 | 1 | BMC communication lost - connected | BMC communication lost - connected | TOO LONG | BMC communication lost - connected 1=Communication link between BMC and SLC is lost. BMC is connected |  | 0 |  |  |  | BOOLEAN |  |  | 1=Communication link between BMC and SLC is lost. BMC is connected
|  |  | 0 | 2 | BMC communication not authenticated | BMC communication not authenticated | TOO LONG | BMC communication not authenticated 1=Communication link between BMC and SLC is not authenticated |  | 0 |  |  |  | BOOLEAN |  |  | 1=Communication link between BMC and SLC is not authenticated
|  |  | 0 | 3 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 4 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 5 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 6 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 7 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 8 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 9 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 10 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 11 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 12 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 13 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 14 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 15 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
40023 | 0x0016 | 22 | 0 |  | Energy Storage | Energy Storage | 14 | Energy Storage | Read Holding Registers | 0 | 40023 | Unsigned 16 bit Integer | 1 | BOOLEAN
|  |  | 0 | 0 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 1 | Modular battery string temperature out of tolerance | Modular battery string temperature out of tolerance | TOO LONG | Modular battery string temperature out of tolerance 1=Modular battery string temperature is out of tolerance |  | 0 |  |  |  | BOOLEAN |  |  | 1=Modular battery string temperature is out of tolerance
|  |  | 0 | 2 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 3 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 4 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 5 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 6 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 7 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 8 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 9 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 10 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 11 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 12 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 13 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 14 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 15 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
40024 | 0x0017 | 23 | 0 |  | Network | Network | 7 | Network | Read Holding Registers | 0 | 40024 | Unsigned 16 bit Integer | 1 | BOOLEAN
|  |  | 0 | 0 | Low temperature threshold violation at remote sensor | Low temperature threshold violation at remote sensor | TOO LONG | Low temperature threshold violation at remote sensor 1=A low temperature threshold violation exists for integrated environmental monitor sensor |  | 0 |  |  |  | BOOLEAN |  |  | 1=A low temperature threshold violation exists for integrated environmental monitor sensor
|  |  | 0 | 1 | Minimum temperature threshols violation at remote sensor | Minimum temperature threshols violation at remote sensor | TOO LONG | Minimum temperature threshols violation at remote sensor 1=A minimum temperature threshold violation exists for integrated environmental monitor sensor |  | 0 |  |  |  | BOOLEAN |  |  | 1=A minimum temperature threshold violation exists for integrated environmental monitor sensor
|  |  | 0 | 2 | High temperature threshold violation at remote sensor | High temperature threshold violation at remote sensor | TOO LONG | High temperature threshold violation at remote sensor 1=A high temperature threshold violation exists for integrated environmental monitor sensor |  | 0 |  |  |  | BOOLEAN |  |  | 1=A high temperature threshold violation exists for integrated environmental monitor sensor
|  |  | 0 | 3 | Maximum temperature threshold violation at remote sensor | Maximum temperature threshold violation at remote sensor | TOO LONG | Maximum temperature threshold violation at remote sensor 1=A maximum temperature threshold violation exists for integrated environmental monitor sensor |  | 0 |  |  |  | BOOLEAN |  |  | 1=A maximum temperature threshold violation exists for integrated environmental monitor sensor
|  |  | 0 | 4 | Low humidity threshold violation at remote sensor | Low humidity threshold violation at remote sensor | TOO LONG | Low humidity threshold violation at remote sensor 1=A low humidity threshold violation exists for integrated environmental monitor sensor |  | 0 |  |  |  | BOOLEAN |  |  | 1=A low humidity threshold violation exists for integrated environmental monitor sensor
|  |  | 0 | 5 | Minimum humidity threshold violation at remote sensor | Minimum humidity threshold violation at remote sensor | TOO LONG | Minimum humidity threshold violation at remote sensor 1=A minimum humidity threshold violation exists for integrated environmental monitor sensor |  | 0 |  |  |  | BOOLEAN |  |  | 1=A minimum humidity threshold violation exists for integrated environmental monitor sensor
|  |  | 0 | 6 | High humidity threshold violation at remote sensor | High humidity threshold violation at remote sensor | TOO LONG | High humidity threshold violation at remote sensor 1=A high humidity threshold violation exists for integrated environmental monitor sensor |  | 0 |  |  |  | BOOLEAN |  |  | 1=A high humidity threshold violation exists for integrated environmental monitor sensor
|  |  | 0 | 7 | Maximum humidity threshold violation at remote sensor | Maximum humidity threshold violation at remote sensor | TOO LONG | Maximum humidity threshold violation at remote sensor 1=A maximum humidity threshold violation exists for integrated environmental monitor sensor |  | 0 |  |  |  | BOOLEAN |  |  | 1=A maximum humidity threshold violation exists for integrated environmental monitor sensor
|  |  | 0 | 8 | Lost communication to remote sensor | Lost communication to remote sensor | TOO LONG | Lost communication to remote sensor 1=Lost the local network management interface-to-integrated environmental monitor communication |  | 0 |  |  |  | BOOLEAN |  |  | 1=Lost the local network management interface-to-integrated environmental monitor communication
|  |  | 0 | 9 | Communication link between NMC and SLC is lost. NMC is disconnected from the system | Communication link between NMC and SLC is lost. NMC is disconnected from the system | TOO LONG | Communication link between NMC and SLC is lost. NMC is disconnected from the system 1=Communication link between NMC and SLC is lost. NMC is disconnected |  | 0 |  |  |  | BOOLEAN |  |  | 1=Communication link between NMC and SLC is lost. NMC is disconnected
|  |  | 0 | 10 | Communication link between NMC and SLC is lost but the NMC is connected to the system | Communication link between NMC and SLC is lost but the NMC is connected to the system | TOO LONG | Communication link between NMC and SLC is lost but the NMC is connected to the system 1=Communication link between NMC and SLC is lost. NMC is connected |  | 0 |  |  |  | BOOLEAN |  |  | 1=Communication link between NMC and SLC is lost. NMC is connected
|  |  | 0 | 11 | Communication link between NMC and SLC is not authenticated | Communication link between NMC and SLC is not authenticated | TOO LONG | Communication link between NMC and SLC is not authenticated 1=Communication link between NMC and SLC is not authenticated |  | 0 |  |  |  | BOOLEAN |  |  | 1=Communication link between NMC and SLC is not authenticated
|  |  | 0 | 12 | NMC firmware incompatible | NMC firmware incompatible | TOO LONG | NMC firmware incompatible 1=Firmware version of the NMC is incompatible |  | 0 |  |  |  | BOOLEAN |  |  | 1=Firmware version of the NMC is incompatible
|  |  | 0 | 13 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 14 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 | 15 | Reserved | Reserved | 8 | Reserved |  | 0 |  |  |  | BOOLEAN
|  |  | 0 |  |  |  | 0 |  |  | 0
Static Data |  |  | 0 |  |  |  | 0 |  |  | 0
44097 | 0x1000 | 4096 | 0 |  | The firmware package version number of the UPS system | UPS Firmware Version | 20 | UPS Firmware Version |  | 0 | 44097 | ASCII | 8 | ASCII
44105 | 0x1008 | 4104 | 0 |  | The hardware version number of the UPS system | UPS Hardware Version | 20 | UPS Hardware Version |  | 0 | 44105 | ASCII | 16 | ASCII
44121 | 0x1018 | 4120 | 0 |  | The UPS model number (commercial reference) | UPS Model Number | 16 | UPS Model Number |  | 0 | 44121 | ASCII | 16 | ASCII
44137 | 0x1028 | 4136 | 0 |  | The UPS serial number | UPS Serial Number | 17 | UPS Serial Number |  | 0 | 44137 | ASCII | 16 | ASCII
44153 | 0x1038 | 4152 | 0 |  | The network management card firmware version number | UPS Network Firmware Version | 28 | UPS Network Firmware Version |  | 0 | 44153 | ASCII | 8 | ASCII
44161 | 0x1040 | 4160 | 0 |  | The network management card hardware version number | UPS Network Hardware Version | 28 | UPS Network Hardware Version |  | 0 | 44161 | ASCII | 16 | ASCII
44177 | 0x1050 | 4176 | 0 |  | The model number (commercial reference) of the network management card | UPS Network Model | 17 | UPS Network Model |  | 0 | 44177 | ASCII | 16 | ASCII
44193 | 0x1060 | 4192 | 0 |  | The network management card serial number | UPS Network Serial Number | 25 | UPS Network Serial Number |  | 0 | 44193 | ASCII | 16 | ASCII
44209 | 0x1070 | 4208 | 4209 |  | Time since battery statistics timer reset (in minutes). | UPS Battery Timer Stats Reset | 33 | UPS Battery Timer Stats Reset min | Read Holding Registers | 44210 | 44209 | Unsigned 32 bit Integer | 2 | UINT32 |  |  | min
44211 | 0x1072 | 4210 | 4211 |  | Total time for UPS in battery operation since battery statistics timer reset (in minutes). | UPS Batt. Operation Time Since Reset | 40 | UPS Batt. Operation Time Since Reset min | Read Holding Registers | 44212 | 44211 | Unsigned 32 bit Integer | 2 | UINT32 |  |  | min
44213 | 0x1074 | 4212 | 4213 |  | Time since operational statistics timer reset (in minutes). | UPS Time OP Stats Since Timer Reset | 39 | UPS Time OP Stats Since Timer Reset min | Read Holding Registers | 44214 | 44213 | Unsigned 32 bit Integer | 2 | UINT32 |  |  | min
44215 | 0x1076 | 4214 | 4215 |  | Total time for UPS in normal operation since operational statistics timer reset (in minutes). | UPS Time Normal Since Timer Reset | 37 | UPS Time Normal Since Timer Reset min | Read Holding Registers | 44216 | 44215 | Unsigned 32 bit Integer | 2 | UINT32 |  |  | min
44217 | 0x1078 | 4216 | 4217 |  | Total time for UPS in bypass operation since operational statistics timer reset (in minutes). | UPS Time Bypass Since Timer Reset | 37 | UPS Time Bypass Since Timer Reset min | Read Holding Registers | 44218 | 44217 | Unsigned 32 bit Integer | 2 | UINT32 |  |  | min
44219 | 0x107A | 4218 | 4219 |  | Total time for UPS in ECOnversion mode since Operational Statistics timer reset (in minutes). | UPS Time ECOnversion Since Reset | 36 | UPS Time ECOnversion Since Reset min | Read Holding Registers | 44220 | 44219 | Unsigned 32 bit Integer | 2 | UINT32 |  |  | min
44221 | 0x107C | 4220 | 4221 |  | Time since the Battery was last replaced (in minutes). | UPS Time Since Battery Replaced | 35 | UPS Time Since Battery Replaced min | Read Holding Registers | 44222 | 44221 | Unsigned 32 bit Integer | 2 | UINT32 |  |  | min
44223 | 0x107E | 4222 | 4223 |  | Time since input energy counter timer reset (in minutes) | UPS Time Since Energy IN Timer Reset | 40 | UPS Time Since Energy IN Timer Reset min | Read Holding Registers | 44224 | 44223 | Unsigned 32 bit Integer | 2 | UINT32 |  |  | min
44225 | 0x1080 | 4224 | 4225 |  | Time since ouput energy counter timer reset (in minutes) | UPS Time Since Energy O Timer Reset | 39 | UPS Time Since Energy O Timer Reset min | Read Holding Registers | 44226 | 44225 | Unsigned 32 bit Integer | 2 | UINT32 |  |  | min
|  |  | 0 |  |  |  | 0 |  |  | 0
Dynamic Data |  |  | 0 |  |  |  | 0 |  |  | 0
44609 | 0x1200 | 4608 | 0 |  | Alarm status of the unit | UPS Alarm Status | 16 | UPS Alarm Status |  | 0 | 44609 |  | 1
|  |  | 0 |  | No alarms present | No alarms present | 37 | No alarms present 0=No alarms present |  | 0 |  |  |  | ENUM |  |  | 0=No alarms present
|  |  | 0 |  | Informational alarm present | Informational alarm present | TOO LONG | Informational alarm present 1=Informational alarm present |  | 0 |  |  |  | ENUM |  |  | 1=Informational alarm present
|  |  | 0 |  | Warning alarm present | Warning alarm present | TOO LONG | Warning alarm present 2=Warning alarm present |  | 0 |  |  |  | ENUM |  |  | 2=Warning alarm present
|  |  | 0 |  | Critical alarm present | Critical alarm present | TOO LONG | Critical alarm present 3=Critical alarm present |  | 0 |  |  |  | ENUM |  |  | 3=Critical alarm present
|  |  | 0 |  |  |  | 0 |  |  | 0
44865 | 0x1300 | 4864 | 0 |  | The present apparent output power for each phase in kVA. Apparent power is the product of RMS (root mean square) volts and RMS amperes (phase1) | Phase A Apparent Output Power | 33 | Phase A Apparent Output Power kVA | Read Holding Registers | 0 | 44865 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | kVA
44866 | 0x1301 | 4865 | 0 |  | The present apparent output power for each phase in kVA. Apparent power is the product of RMS (root mean square) volts and RMS amperes (phase2) | Phase B Apparent Output Power | 33 | Phase B Apparent Output Power kVA | Read Holding Registers | 0 | 44866 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | kVA
44867 | 0x1302 | 4866 | 0 |  | The present apparent output power for each phase in kVA. Apparent power is the product of RMS (root mean square) volts and RMS amperes (phase3) | Phase C Apparent Output Power | 33 | Phase C Apparent Output Power kVA | Read Holding Registers | 0 | 44867 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | kVA
44868 | 0x1303 | 4867 | 0 |  | The present output current for each phase in A (phase1) | Phase A Output Current | 24 | Phase A Output Current A | Read Holding Registers | 0 | 44868 | Unsigned 16 bit Integer | 1 | UINT16 | 0.01 | 100 | A
44869 | 0x1304 | 4868 | 0 |  | The present output current for each phase in A (phase2) | Phase B Output Current | 24 | Phase B Output Current A | Read Holding Registers | 0 | 44869 | Unsigned 16 bit Integer | 1 | UINT16 | 0.01 | 100 | A
44870 | 0x1305 | 4869 | 0 |  | The present output current for each phase in A (phase3) | Phase C Output Current | 24 | Phase C Output Current A | Read Holding Registers | 0 | 44870 | Unsigned 16 bit Integer | 1 | UINT16 | 0.01 | 100 | A
44871 | 0x1306 | 4870 | 0 |  | The present output crest factor for each phase. The output crest factor is the ratio of the peak value of the output current to the RMS (root mean square) value (phase1) | Phase A Output Crest Factor | 27 | Phase A Output Crest Factor | Read Holding Registers | 0 | 44871 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10
44872 | 0x1307 | 4871 | 0 |  | The present output crest factor for each phase. The output crest factor is the ratio of the peak value of the output current to the RMS (root mean square) value (phase2) | Phase B Output Crest Factor | 27 | Phase B Output Crest Factor | Read Holding Registers | 0 | 44872 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10
44873 | 0x1308 | 4872 | 0 |  | The present output crest factor for each phase. The output crest factor is the ratio of the peak value of the output current to the RMS (root mean square) value (phase3) | Phase C Output Crest Factor | 27 | Phase C Output Crest Factor | Read Holding Registers | 0 | 44873 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10
44874 | 0x1309 | 4873 | 0 |  | The THD (total harmonic distortion) for each phase, as a percentage, for the present output current (phase1) | Phase A Output THD | 20 | Phase A Output THD % | Read Holding Registers | 0 | 44874 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | %
44875 | 0x130A | 4874 | 0 |  | The THD (total harmonic distortion) for each phase, as a percentage, for the present output current (phase2) | Phase B Output THD | 20 | Phase B Output THD % | Read Holding Registers | 0 | 44875 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | %
44876 | 0x130B | 4875 | 0 |  | The THD (total harmonic distortion) for each phase, as a percentage, for the present output current (phase3) | Phase C Output THD | 20 | Phase C Output THD % | Read Holding Registers | 0 | 44876 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | %
44877 | 0x130C | 4876 | 0 |  | The present output power factor for each phase. Power factor is the ratio of active power to apparent power (phase1) | Phase A Output Power Factor | 27 | Phase A Output Power Factor | Read Holding Registers | 0 | 44877 | Unsigned 16 bit Integer | 1 | UINT16 | 0.01 | 100
44878 | 0x130D | 4877 | 0 |  | The present output power factor for each phase. Power factor is the ratio of active power to apparent power (phase2) | Phase B Output Power Factor | 27 | Phase B Output Power Factor | Read Holding Registers | 0 | 44878 | Unsigned 16 bit Integer | 1 | UINT16 | 0.01 | 100
44879 | 0x130E | 4878 | 0 |  | The present output power factor for each phase. Power factor is the ratio of active power to apparent power (phase3) | Phase C Output Power Factor | 27 | Phase C Output Power Factor | Read Holding Registers | 0 | 44879 | Unsigned 16 bit Integer | 1 | UINT16 | 0.01 | 100
44880 | 0x130F | 4879 | 0 |  | The present active (or real) output power for each phase in kW. Active power is the portion of power flow that, averaged over a complete cycle of the AC waveform, results in net transfer of energy in one direction (phase1) | Phase A Output Real Power | 28 | Phase A Output Real Power kW | Read Holding Registers | 0 | 44880 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | kW
44881 | 0x1310 | 4880 | 0 |  | The present active (or real) output power for each phase in kW. Active power is the portion of power flow that, averaged over a complete cycle of the AC waveform, results in net transfer of energy in one direction (phase2) | Phase B Output Real Power | 28 | Phase B Output Real Power kW | Read Holding Registers | 0 | 44881 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | kW
44882 | 0x1311 | 4881 | 0 |  | The present active (or real) output power for each phase in kW. Active power is the portion of power flow that, averaged over a complete cycle of the AC waveform, results in net transfer of energy in one direction (phase3) | Phase C Output Real Power | 28 | Phase C Output Real Power kW | Read Holding Registers | 0 | 44882 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | kW
44883 | 0x1312 | 4882 | 0 |  | The present output voltage for each phase (phase1) | Phase A Output Voltage | 24 | Phase A Output Voltage V | Read Holding Registers | 0 | 44883 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | V
44884 | 0x1313 | 4883 | 0 |  | The present output voltage for each phase (phase2) | Phase B Output Voltage | 24 | Phase B Output Voltage V | Read Holding Registers | 0 | 44884 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | V
44885 | 0x1314 | 4884 | 0 |  | The present output voltage for each phase (phase3) | Phase C Output Voltage | 24 | Phase C Output Voltage V | Read Holding Registers | 0 | 44885 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | V
44886 | 0x1315 | 4885 | 0 |  | The present phase-to-phase output RMS voltage (phase1) | Phase A-B Output Voltage | 26 | Phase A-B Output Voltage V | Read Holding Registers | 0 | 44886 | Unsigned 16 bit Integer | 1 | UINT16 | 0.01 | 100 | V
44887 | 0x1316 | 4886 | 0 |  | The present phase-to-phase output RMS voltage (phase2) | Phase B-C Output Voltage | 26 | Phase B-C Output Voltage V | Read Holding Registers | 0 | 44887 | Unsigned 16 bit Integer | 1 | UINT16 | 0.01 | 100 | V
44888 | 0x1317 | 4887 | 0 |  | The present phase-to-phase output RMS voltage (phase3) | Phase C-A Output Voltage | 26 | Phase C-A Output Voltage V | Read Holding Registers | 0 | 44888 | Unsigned 16 bit Integer | 1 | UINT16 | 0.01 | 100 | V
44889 | 0x1318 | 4888 | 0 |  | The present total apparent output power in kVA. Apparent power is the product of RMS (root mean square) volts and RMS amperes | Total Apparent Output Power | 31 | Total Apparent Output Power kVA | Read Holding Registers | 0 | 44889 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | kVA
44890 | 0x1319 | 4889 | 0 |  | Output current as percentage of total available current (highest phase) | Percent of Highest Output Current | 35 | Percent of Highest Output Current % | Read Holding Registers | 0 | 44890 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | %
44891 | 0x131A | 4890 | 0 |  | The present output frequency in Hz | Output Frequency | 19 | Output Frequency Hz | Read Holding Registers | 0 | 44891 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | Hz
44892 | 0x131B | 4891 | 0 |  | The present total active (or real) output power (for all three phases) in kW | Total Real Output Power | 26 | Total Real Output Power kW | Read Holding Registers | 0 | 44892 | Unsigned 16 bit Integer | 1 | UINT16 | 0.01 | 100 | kW
44893 | 0x131C | 4892 | 4893 |  | The total energy supplied since the time of installation or since the counter was reset | Cumulative Energy Supplied | 30 | Cumulative Energy Supplied kWh | Read Holding Registers | 44894 | 44893 | Unsigned 32 bit Integer | 2 | UINT32 | 0.1 | 10 | kWh
44895 | 0x131E | 4894 | 0 |  | The present output neutral current in A | Phase N Output Current | 24 | Phase N Output Current A | Read Holding Registers | 0 | 44895 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | A
|  |  | 0 |  |  |  | 0 |  |  | 0
45121 | 0x1400 | 5120 | 0 |  | The present apparent input power for each phase in kVA. Apparent power is the product of RMS (root mean square) volts and RMS amperes (phase1) | Phase A Apparent Input Power | 32 | Phase A Apparent Input Power kVA | Read Holding Registers | 0 | 45121 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | kVA
45122 | 0x1401 | 5121 | 0 |  | The present apparent input power for each phase in kVA. Apparent power is the product of RMS (root mean square) volts and RMS amperes (phase2) | Phase B Apparent Input Power | 32 | Phase B Apparent Input Power kVA | Read Holding Registers | 0 | 45122 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | kVA
45123 | 0x1402 | 5122 | 0 |  | The present apparent input power for each phase in kVA. Apparent power is the product of RMS (root mean square) volts and RMS amperes (phase3) | Phase C Apparent Input Power | 32 | Phase C Apparent Input Power kVA | Read Holding Registers | 0 | 45123 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | kVA
45124 | 0x1403 | 5123 | 0 |  | The present input current for each phase in A (phase1) | Phase A Input Current | 23 | Phase A Input Current A | Read Holding Registers | 0 | 45124 | Unsigned 16 bit Integer | 1 | UINT16 | 0.01 | 100 | A
45125 | 0x1404 | 5124 | 0 |  | The present input current for each phase in A (phase2) | Phase B Input Current | 23 | Phase B Input Current A | Read Holding Registers | 0 | 45125 | Unsigned 16 bit Integer | 1 | UINT16 | 0.01 | 100 | A
45126 | 0x1405 | 5125 | 0 |  | The present input current for each phase in A (phase3) | Phase C Input Current | 23 | Phase C Input Current A | Read Holding Registers | 0 | 45126 | Unsigned 16 bit Integer | 1 | UINT16 | 0.01 | 100 | A
45127 | 0x1406 | 5126 | 0 |  | The ratio of the active power to the apparent power (phase1) | Phase A Input Power Factor | 26 | Phase A Input Power Factor | Read Holding Registers | 0 | 45127 | Unsigned 16 bit Integer | 1 | UINT16 | 0.01 | 100
45128 | 0x1407 | 5127 | 0 |  | The ratio of the active power to the apparent power (phase2) | Phase B Input Power Factor | 26 | Phase B Input Power Factor | Read Holding Registers | 0 | 45128 | Unsigned 16 bit Integer | 1 | UINT16 | 0.01 | 100
45129 | 0x1408 | 5128 | 0 |  | The ratio of the active power to the apparent power (phase3) | Phase C Input Power Factor | 26 | Phase C Input Power Factor | Read Holding Registers | 0 | 45129 | Unsigned 16 bit Integer | 1 | UINT16 | 0.01 | 100
45130 | 0x1409 | 5129 | 0 |  | The present active (or real) input power for each phase in kW. Active power is the portion of power flow that, averaged over a complete cycle of the AC waveform, results in net transfer of energy in one direction (phase1) | Phase A Input Real Power | 27 | Phase A Input Real Power kW | Read Holding Registers | 0 | 45130 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | kW
45131 | 0x140A | 5130 | 0 |  | The present active (or real) input power for each phase in kW. Active power is the portion of power flow that, averaged over a complete cycle of the AC waveform, results in net transfer of energy in one direction (phase2) | Phase B Input Real Power | 27 | Phase B Input Real Power kW | Read Holding Registers | 0 | 45131 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | kW
45132 | 0x140B | 5131 | 0 |  | The present active (or real) input power for each phase in kW. Active power is the portion of power flow that, averaged over a complete cycle of the AC waveform, results in net transfer of energy in one direction (phase3) | Phase C Input Real Power | 27 | Phase C Input Real Power kW | Read Holding Registers | 0 | 45132 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | kW
45133 | 0x140C | 5132 | 0 |  | The present input voltage for each phase (phase1) | Phase A Input Voltage | 23 | Phase A Input Voltage V | Read Holding Registers | 0 | 45133 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | V
45134 | 0x140D | 5133 | 0 |  | The present input voltage for each phase (phase2) | Phase B Input Voltage | 23 | Phase B Input Voltage V | Read Holding Registers | 0 | 45134 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | V
45135 | 0x140E | 5134 | 0 |  | The present input voltage for each phase (phase3) | Phase C Input Voltage | 23 | Phase C Input Voltage V | Read Holding Registers | 0 | 45135 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | V
45136 | 0x140F | 5135 | 0 |  | The present phase-to-phase input RMS voltage (phase1) | Phase A-B Input Voltage | 25 | Phase A-B Input Voltage V | Read Holding Registers | 0 | 45136 | Unsigned 16 bit Integer | 1 | UINT16 | 0.01 | 100 | V
45137 | 0x1410 | 5136 | 0 |  | The present phase-to-phase input RMS voltage (phase2) | Phase B-C Input Voltage | 25 | Phase B-C Input Voltage V | Read Holding Registers | 0 | 45137 | Unsigned 16 bit Integer | 1 | UINT16 | 0.01 | 100 | V
45138 | 0x1411 | 5137 | 0 |  | The present phase-to-phase input RMS voltage (phase3) | Phase C-A Input Voltage | 25 | Phase C-A Input Voltage V | Read Holding Registers | 0 | 45138 | Unsigned 16 bit Integer | 1 | UINT16 | 0.01 | 100 | V
45139 | 0x1412 | 5138 | 0 |  | The present total apparent power input (for all three phases) in kVA | Total Apparent Input Power | 30 | Total Apparent Input Power kVA | Read Holding Registers | 0 | 45139 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | kVA
45140 | 0x1413 | 5139 | 0 |  | The present input frequency in Hz | Input Frequency | 18 | Input Frequency Hz | Read Holding Registers | 0 | 45140 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | Hz
45141 | 0x1414 | 5140 | 0 |  | The present total real power (or active power) input (for all three phases) in kW | Total Real Input Power | 25 | Total Real Input Power kW | Read Holding Registers | 0 | 45141 | Unsigned 16 bit Integer | 1 | UINT16 | 0.01 | 100 | kW
45142 | 0x1415 | 5141 | 5142 |  | The total energy consumption since the time of installation or since the counter was reset. | Cumulative Energy Consumption | 33 | Cumulative Energy Consumption kWh | Read Holding Registers | 45143 | 45142 | Unsigned 32 bit Integer | 2 | UINT32 | 0.1 | 10 | kWh
|  |  | 0 |  |  |  | 0 |  |  | 0
45377 | 0x1500 | 5376 | 0 |  | The present apparent bypass power for each phase in kVA. Apparent power is the product of RMS (root mean square) volts and RMS amperes (phase1) | Phase A Apparent Bypass Input Power | 39 | Phase A Apparent Bypass Input Power kVA | Read Holding Registers | 0 | 45377 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | kVA
45378 | 0x1501 | 5377 | 0 |  | The present apparent bypass power for each phase in kVA. Apparent power is the product of RMS (root mean square) volts and RMS amperes (phase2) | Phase B Apparent Bypass Input Power | 39 | Phase B Apparent Bypass Input Power kVA | Read Holding Registers | 0 | 45378 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | kVA
45379 | 0x1502 | 5378 | 0 |  | The present apparent bypass power for each phase in kVA. Apparent power is the product of RMS (root mean square) volts and RMS amperes (phase3) | Phase C Apparent Bypass Input Power | 39 | Phase C Apparent Bypass Input Power kVA | Read Holding Registers | 0 | 45379 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | kVA
45380 | 0x1503 | 5379 | 0 |  | The present bypass current for each phase in A (phase1) | Phase A Input Current Bypass | 30 | Phase A Input Current Bypass A | Read Holding Registers | 0 | 45380 | Unsigned 16 bit Integer | 1 | UINT16 | 0.01 | 100 | A
45381 | 0x1504 | 5380 | 0 |  | The present bypass current for each phase in A (phase2) | Phase B Input Current Bypass | 30 | Phase B Input Current Bypass A | Read Holding Registers | 0 | 45381 | Unsigned 16 bit Integer | 1 | UINT16 | 0.01 | 100 | A
45382 | 0x1505 | 5381 | 0 |  | The present bypass current for each phase in A (phase3) | Phase C Input Current Bypass | 30 | Phase C Input Current Bypass A | Read Holding Registers | 0 | 45382 | Unsigned 16 bit Integer | 1 | UINT16 | 0.01 | 100 | A
45383 | 0x1506 | 5382 | 0 |  | The present bypass power factor for each phase. Power factor is the ratio of active power to apparent power (phase1) | Phase A Input Bypass Power Factor | 33 | Phase A Input Bypass Power Factor | Read Holding Registers | 0 | 45383 | Unsigned 16 bit Integer | 1 | UINT16 | 0.01 | 100
45384 | 0x1507 | 5383 | 0 |  | The present bypass power factor for each phase. Power factor is the ratio of active power to apparent power (phase2) | Phase B Input Bypass Power Factor | 33 | Phase B Input Bypass Power Factor | Read Holding Registers | 0 | 45384 | Unsigned 16 bit Integer | 1 | UINT16 | 0.01 | 100
45385 | 0x1508 | 5384 | 0 |  | The present bypass power factor for each phase. Power factor is the ratio of active power to apparent power (phase3) | Phase C Input Bypass Power Factor | 33 | Phase C Input Bypass Power Factor | Read Holding Registers | 0 | 45385 | Unsigned 16 bit Integer | 1 | UINT16 | 0.01 | 100
45386 | 0x1509 | 5385 | 0 |  | The present active (or real) bypass power for each phase in kW. Active power is the time average of the instantaneous product of voltage and current (phase1) | Phase A Input Real Bypass Power | 34 | Phase A Input Real Bypass Power kW | Read Holding Registers | 0 | 45386 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | kW
45387 | 0x150A | 5386 | 0 |  | The present active (or real) bypass power for each phase in kW. Active power is the time average of the instantaneous product of voltage and current (phase2) | Phase B Input Real Bypass Power | 34 | Phase B Input Real Bypass Power kW | Read Holding Registers | 0 | 45387 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | kW
45388 | 0x150B | 5387 | 0 |  | The present active (or real) bypass power for each phase in kW. Active power is the time average of the instantaneous product of voltage and current (phase3) | Phase C Input Real Bypass Power | 34 | Phase C Input Real Bypass Power kW | Read Holding Registers | 0 | 45388 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | kW
45389 | 0x150C | 5388 | 0 |  | The present bypass voltage for each phase (phase1) | Phase A Input Bypass Voltage | 30 | Phase A Input Bypass Voltage V | Read Holding Registers | 0 | 45389 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | V
45390 | 0x150D | 5389 | 0 |  | The present bypass voltage for each phase (phase2) | Phase B Input Bypass Voltage | 30 | Phase B Input Bypass Voltage V | Read Holding Registers | 0 | 45390 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | V
45391 | 0x150E | 5390 | 0 |  | The present bypass voltage for each phase (phase3) | Phase C Input Bypass Voltage | 30 | Phase C Input Bypass Voltage V | Read Holding Registers | 0 | 45391 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | V
45392 | 0x150F | 5391 | 0 |  | The present phase-to-phase bypass RMS voltage (V). (phase1) | Phase A-B Input Bypass Voltage | 32 | Phase A-B Input Bypass Voltage V | Read Holding Registers | 0 | 45392 | Unsigned 16 bit Integer | 1 | UINT16 | 0.01 | 100 | V
45393 | 0x1510 | 5392 | 0 |  | The present phase-to-phase bypass RMS voltage (V). (phase2) | Phase B-C Input Bypass Voltage | 32 | Phase B-C Input Bypass Voltage V | Read Holding Registers | 0 | 45393 | Unsigned 16 bit Integer | 1 | UINT16 | 0.01 | 100 | V
45394 | 0x1511 | 5393 | 0 |  | The present phase-to-phase bypass RMS voltage (V). (phase3) | Phase C-A Input Bypass Voltage | 32 | Phase C-A Input Bypass Voltage V | Read Holding Registers | 0 | 45394 | Unsigned 16 bit Integer | 1 | UINT16 | 0.01 | 100 | V
45395 | 0x1512 | 5394 | 0 |  | The present total apparent bypass power (for all three phases) in kVA | Total Apparent Input Bypass Power | 37 | Total Apparent Input Bypass Power kVA | Read Holding Registers | 0 | 45395 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | kVA
45396 | 0x1513 | 5395 | 0 |  | The present bypass frequency in Hz | Input Bypass Frequency | 25 | Input Bypass Frequency Hz | Read Holding Registers | 0 | 45396 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | Hz
45397 | 0x1514 | 5396 | 0 |  | The present total active bypass power (for all three phases) in kW | Total Real Input Bypass Power | 32 | Total Real Input Bypass Power kW | Read Holding Registers | 0 | 45397 | Unsigned 16 bit Integer | 1 | UINT16 | 0.01 | 100 | kW
|  |  | 0 |  |  |  | 0 |  |  | 0
45633 | 0x1600 | 5632 | 0 |  | The general condition of the charger | Battery Charger Condition | 25 | Battery Charger Condition |  | 0 | 45633 |  | 1
|  |  | 0 |  | Float charging | Float charging | 31 | Float charging 0=Float charging |  | 0 |  |  |  | ENUM |  |  | 0=Float charging
|  |  | 0 |  | Boost charging | Boost charging | 31 | Boost charging 1=Boost charging |  | 0 |  |  |  | ENUM |  |  | 1=Boost charging
|  |  | 0 |  | Cyclic resting | Cyclic resting | 31 | Cyclic resting 2=Cyclic resting |  | 0 |  |  |  | ENUM |  |  | 2=Cyclic resting
|  |  | 0 |  | Not charging | Not charging | 27 | Not charging 3=Not charging |  | 0 |  |  |  | ENUM |  |  | 3=Not charging
|  |  | 0 |  | Equalization charging | Equalization charging | TOO LONG | Equalization charging 4=Equalization charging |  | 0 |  |  |  | ENUM |  |  | 4=Equalization charging
|  |  | 0 |  | Test in progress | Test in progress | 35 | Test in progress 5=Test in progress |  | 0 |  |  |  | ENUM |  |  | 5=Test in progress
|  |  | 0 |  | Cyclic float charging | Cyclic float charging | TOO LONG | Cyclic float charging 6=Cyclic float charging |  | 0 |  |  |  | ENUM |  |  | 6=Cyclic float charging
45634 | 0x1601 | 5633 | 0 |  | The highest battery temperature from the connected temperature sensors | Battery Highest Temperature | 35 | Battery Highest Temperature Celsius | Read Holding Registers | 0 | 45634 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | Celsius
45635 | 0x1602 | 5634 | 0 |  | The present DC power being drawn from the battery in kW | Battery Power Drawn | 22 | Battery Power Drawn kW | Read Holding Registers | 0 | 45635 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | kW
45636 | 0x1603 | 5635 | 0 |  | Combined status for battery breakers. | Battery Breakers Status | 23 | Battery Breakers Status |  | 0 | 45636 |  | 1
|  |  | 0 |  | Open | Open | 11 | Open 0=Open |  | 0 |  |  |  | ENUM |  |  | 0=Open
|  |  | 0 |  | Closed | Closed | 15 | Closed 1=Closed |  | 0 |  |  |  | ENUM |  |  | 1=Closed
45637 | 0x1604 | 5636 | 5637 |  | The amount of time before the batteries reach the low-voltage shutdown level | Battery Low Volt. Shutdown Est. Time | 40 | Battery Low Volt. Shutdown Est. Time Sec | Read Holding Registers | 45638 | 45637 | Unsigned 32 bit Integer | 2 | UINT32 | 1 | 1 | Sec
45639 | 0x1606 | 5638 | 5639 |  | Estimated time for recharging the battery | Battery Recharge Estimated Time | 35 | Battery Recharge Estimated Time Sec | Read Holding Registers | 45640 | 45639 | Unsigned 32 bit Integer | 2 | UINT32 | 1 | 1 | Sec
45641 | 0x1608 | 5640 | 0 |  | The present battery charge, as a percentage of full charge capacity | Battery Charge Percentage | 27 | Battery Charge Percentage % | Read Holding Registers | 0 | 45641 | Unsigned 16 bit Integer | 1 | UINT16 | 1 | 1 | %
45642 | 0x1609 | 5641 | 0 |  | The present battery voltage (V) | Battery Voltage | 17 | Battery Voltage V | Read Holding Registers | 0 | 45642 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | V
45643 | 0x160A | 5642 | 0 |  | The present battery current (A). A positive current indicates that the battery is charging; a negative current indicates that the battery is discharging. | Battery Current Drawn | 23 | Battery Current Drawn A | Read Holding Registers | 0 | 45643 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | A
45644 | 0x160B | 5643 | 0 |  | Status of battery self-test. Can indicate the battery test status triggered by user-commanded or scheduled self-test | Battery Self-test Status | 24 | Battery Self-test Status |  | 0 | 45644 |  | 1
|  |  | 0 |  | Battery self-test is inactive | Battery self-test is inactive | TOO LONG | Battery self-test is inactive 0=Battery self test is inactive |  | 0 |  |  |  | ENUM |  |  | 0=Battery self test is inactive
|  |  | 0 |  | Battery self-test is running | Battery self-test is running | TOO LONG | Battery self-test is running 1=Battery self test is running |  | 0 |  |  |  | ENUM |  |  | 1=Battery self test is running
|  |  | 0 |  | Battery self-test is aborted because the system detects a critical alarm | Battery self-test is aborted because the system detects a critical alarm | TOO LONG | Battery self-test is aborted because the system detects a critical alarm 2=Battery self-test is aborted because the system detects a critical alarm |  | 0 |  |  |  | ENUM |  |  | 2=Battery self-test is aborted because the system detects a critical alarm
|  |  | 0 |  | Battery self-test is aborted due to user command | Battery self-test is aborted due to user command | TOO LONG | Battery self-test is aborted due to user command 3=Battery self test is aborted due to user command |  | 0 |  |  |  | ENUM |  |  | 3=Battery self test is aborted due to user command
|  |  | 0 |  | Battery self-test is completed | Battery self-test is completed | TOO LONG | Battery self-test is completed 4=Battery self test is completed |  | 0 |  |  |  | ENUM |  |  | 4=Battery self test is completed
45645 | 0x160C | 5644 | 0 |  | Status indicates the battery health state result from battery test | Battery Health State from Self-test | 35 | Battery Health State from Self-test |  | 0 | 45645 |  | 1
|  |  | 0 |  | Battery condition is OK | Battery condition is OK | TOO LONG | Battery condition is OK 0=Battery condition is OK |  | 0 |  |  |  | ENUM |  |  | 0=Battery condition is OK
|  |  | 0 |  | Battery condition is unknown | Battery condition is unknown | TOO LONG | Battery condition is unknown 1=Battery condition is unknown |  | 0 |  |  |  | ENUM |  |  | 1=Battery condition is unknown
|  |  | 0 |  | Battery condition is weak | Battery condition is weak | TOO LONG | Battery condition is weak 2=Battery condition is weak |  | 0 |  |  |  | ENUM |  |  | 2=Battery condition is weak
|  |  | 0 |  | Battery condition is poor | Battery condition is poor | TOO LONG | Battery condition is poor 3=Battery condition is poor |  | 0 |  |  |  | ENUM |  |  | 3=Battery condition is poor
45646 | 0x160D | 5645 | 0 |  | The operation mode of the charger | Battery Charger Operation Mode | 30 | Battery Charger Operation Mode |  | 0 | 45646 |  | 1
|  |  | 0 |  | Battery is resting | Battery is resting | 39 | Battery is resting 0=Battery is resting |  | 0 |  |  |  | ENUM |  |  | 0=Battery is resting
|  |  | 0 |  | Battery is charging | Battery is charging | TOO LONG | Battery is charging 1=Battery is charging |  | 0 |  |  |  | ENUM |  |  | 1=Battery is charging
|  |  | 0 |  | Battery is discharging | Battery is discharging | TOO LONG | Battery is discharging 2=Battery is discharging |  | 0 |  |  |  | ENUM |  |  | 2=Battery is discharging
45647 | 0x160E | 5646 | 0 |  | Measurement of the total available battery capacity in Ah for the UPS | Battery Total Energy Capacity | 32 | Battery Total Energy Capacity Ah | Read Holding Registers | 0 | 45647 | Unsigned 16 bit Integer | 1 | UINT16 | 1 | 1 | Ah
45648 | 0x160F | 5647 | 0 |  | Status that indicates if there are battery modules from different vendors installed in the modular battery system (not on string level but on system level) | Battery Third-Party Modules | 27 | Battery Third-Party Modules |  | 0 | 45648 |  | 1
|  |  | 0 |  | State is OK | State is OK | 25 | State is OK 0=State is OK |  | 0 |  |  |  | ENUM |  |  | 0=State is OK
|  |  | 0 |  | State is not OK | State is not OK | 33 | State is not OK 1=State is not OK |  | 0 |  |  |  | ENUM |  |  | 1=State is not OK
45649 | 0x1610 | 5648 | 0 |  | Modular battery DC relay status | Battery Modular DC Relay Status | 31 | Battery Modular DC Relay Status |  | 0 | 45649 |  | 1
|  |  | 0 |  | Breaker is opened | Breaker is opened | 37 | Breaker is opened 0=Breaker is opened |  | 0 |  |  |  | ENUM |  |  | 0=Breaker is opened
|  |  | 0 |  | Breaker is closed | Breaker is closed | 37 | Breaker is closed 1=Breaker is closed |  | 0 |  |  |  | ENUM |  |  | 1=Breaker is closed
|  |  | 0 |  |  |  | 0 |  |  | 0
45889 | 0x1700 | 5888 | 0 |  | Switchgear system status | Switchgear System Status | 24 | Switchgear System Status |  | 0 | 45889 |  | 1
|  |  | 0 | 0 | Unit input breaker (UIB) status | Unit input breaker (UIB) status | 40 | Unit input breaker (UIB) status 1=Closed |  | 0 |  |  |  | BOOLEAN |  |  | 1=Closed
|  |  | 0 | 1 | Unit output breaker (UOB) status | Unit output breaker (UOB) status | TOO LONG | Unit output breaker (UOB) status 1=Closed |  | 0 |  |  |  | BOOLEAN |  |  | 1=Closed
|  |  | 0 | 2 | Static switch input breaker (SSIB) status | Static switch input breaker (SSIB) status | TOO LONG | Static switch input breaker (SSIB) status 1=Closed |  | 0 |  |  |  | BOOLEAN |  |  | 1=Closed
|  |  | 0 | 3 | Internal maintenance bypass breaker (IMB) status | Internal maintenance bypass breaker (IMB) status | TOO LONG | Internal maintenance bypass breaker (IMB) status 1=Closed |  | 0 |  |  |  | BOOLEAN |  |  | 1=Closed
|  |  | 0 | 4 | Maintenance bypass breaker (MBB) status | Maintenance bypass breaker (MBB) status | TOO LONG | Maintenance bypass breaker (MBB) status 1=Closed |  | 0 |  |  |  | BOOLEAN |  |  | 1=Closed
|  |  | 0 | 5 | Redundant internal maintenance bypass breaker (RIMB) status | Redundant internal maintenance bypass breaker (RIMB) status | TOO LONG | Redundant internal maintenance bypass breaker (RIMB) status 1=Closed |  | 0 |  |  |  | BOOLEAN |  |  | 1=Closed
|  |  | 0 | 6 | System isolation breaker (SIB) status | System isolation breaker (SIB) status | TOO LONG | System isolation breaker (SIB) status 1=Closed |  | 0 |  |  |  | BOOLEAN |  |  | 1=Closed
45890 | 0x1701 | 5889 | 0 |  | Status of the firmware upgrade process | Firmware Upgrade Status | 23 | Firmware Upgrade Status |  | 0 | 45890 |  | 1
|  |  | 0 |  | Firmware update in INIT state | Firmware update in INIT state | TOO LONG | Firmware update in INIT state 0=Firmware update in INIT state |  | 0 |  |  |  | ENUM |  |  | 0=Firmware update in INIT state
|  |  | 0 |  | Firmware update in IDLE State | Firmware update in IDLE State | TOO LONG | Firmware update in IDLE State 1=Firmware update in IDLE State |  | 0 |  |  |  | ENUM |  |  | 1=Firmware update in IDLE State
|  |  | 0 |  | Firmware package is DOWNLOADING | Firmware package is DOWNLOADING | TOO LONG | Firmware package is DOWNLOADING 2=Firmware package is DOWNLOADING |  | 0 |  |  |  | ENUM |  |  | 2=Firmware package is DOWNLOADING
|  |  | 0 |  | Firmware package is INSTALLING | Firmware package is INSTALLING | TOO LONG | Firmware package is INSTALLING 3=Firmware package is INSTALLING |  | 0 |  |  |  | ENUM |  |  | 3=Firmware package is INSTALLING
|  |  | 0 |  | Firmware package is in REBOOTING state | Firmware package is in REBOOTING state | TOO LONG | Firmware package is in REBOOTING state 4=Firmware package is in REBOOTING state |  | 0 |  |  |  | ENUM |  |  | 4=Firmware package is in REBOOTING state
|  |  | 0 |  | Firmware update in FULL_SYS_UPDATE_FAIL state | Firmware update in FULL_SYS_UPDATE_FAIL state | TOO LONG | Firmware update in FULL_SYS_UPDATE_FAIL state 5=Firmware update in FULL_SYS_UPDATE_FAIL state |  | 0 |  |  |  | ENUM |  |  | 5=Firmware update in FULL_SYS_UPDATE_FAIL state
|  |  | 0 |  | Firmware update in FULL_SYS_UPDATE_DONE state | Firmware update in FULL_SYS_UPDATE_DONE state | TOO LONG | Firmware update in FULL_SYS_UPDATE_DONE state 6=Firmware update in FULL_SYS_UPDATE_DONE state |  | 0 |  |  |  | ENUM |  |  | 6=Firmware update in FULL_SYS_UPDATE_DONE state
|  |  | 0 |  | Firmware update in FULL_SYS_UPDATE_ABORTED state | Firmware update in FULL_SYS_UPDATE_ABORTED state | TOO LONG | Firmware update in FULL_SYS_UPDATE_ABORTED state 7=Firmware update in FULL_SYS_UPDATE_ABORTED state |  | 0 |  |  |  | ENUM |  |  | 7=Firmware update in FULL_SYS_UPDATE_ABORTED state
|  |  | 0 |  | Firmware update in SPARE_PART_UPDATE state | Firmware update in SPARE_PART_UPDATE state | TOO LONG | Firmware update in SPARE_PART_UPDATE state 8=Firmware update in SPARE_PART_UPDATE state |  | 0 |  |  |  | ENUM |  |  | 8=Firmware update in SPARE_PART_UPDATE state
|  |  | 0 |  | Firmware update did not succeed | Firmware update did not succeed | TOO LONG | Firmware update did not succeed 9=Firmware update did not succeed |  | 0 |  |  |  | ENUM |  |  | 9=Firmware update did not succeed
45891 | 0x1702 | 5890 | 0 |  | Reserved | Reserved 4 | 10 | Reserved 4 |  | 0 | 45891 |  | 1
45892 | 0x1703 | 5891 | 0 |  | The present operation mode of the complete UPS system | UPS Complete System Operation Mode | 34 | UPS Complete System Operation Mode |  | 0 | 45892 |  | 1
|  |  | 0 |  | System: off operation | System: off operation | TOO LONG | System: off operation 0=System is in off operation |  | 0 |  |  |  | ENUM |  |  | 0=System is in off operation
|  |  | 0 |  | System: inverter operation | System: inverter operation | TOO LONG | System: inverter operation 1=System is in inverter operation |  | 0 |  |  |  | ENUM |  |  | 1=System is in inverter operation
|  |  | 0 |  | System: forced static bypass operation | System: forced static bypass operation | TOO LONG | System: forced static bypass operation 2=System is in forced static bypass operation |  | 0 |  |  |  | ENUM |  |  | 2=System is in forced static bypass operation
|  |  | 0 |  | System: requested static bypass operation | System: requested static bypass operation | TOO LONG | System: requested static bypass operation 3=System is in requested static bypass operation |  | 0 |  |  |  | ENUM |  |  | 3=System is in requested static bypass operation
|  |  | 0 |  | System: maintenance bypass operation | System: maintenance bypass operation | TOO LONG | System: maintenance bypass operation 4=System is in maintenance bypass operation |  | 0 |  |  |  | ENUM |  |  | 4=System is in maintenance bypass operation
|  |  | 0 |  | System: static bypass standby operation | System: static bypass standby operation | TOO LONG | System: static bypass standby operation 5=System is in static bypass standby operation |  | 0 |  |  |  | ENUM |  |  | 5=System is in static bypass standby operation
|  |  | 0 |  | System: ECOnversion mode | System: ECOnversion mode | TOO LONG | System: ECOnversion mode 6=System is in ECOnversion mode |  | 0 |  |  |  | ENUM |  |  | 6=System is in ECOnversion mode
|  |  | 0 |  | System: ECO mode | System: ECO mode | 40 | System: ECO mode 7=System is in ECO mode |  | 0 |  |  |  | ENUM |  |  | 7=System is in ECO mode
45893 | 0x1704 | 5892 | 0 |  | The present operation mode of the UPS | UPS Operation Mode | 18 | UPS Operation Mode |  | 0 | 45893 |  | 1
|  |  | 0 |  | UPS: initialize operation | UPS: initialize operation | TOO LONG | UPS: initialize operation 0=UPS is in is in initialize operation |  | 0 |  |  |  | ENUM |  |  | 0=UPS is in is in initialize operation
|  |  | 0 |  | UPS: off operation | UPS: off operation | TOO LONG | UPS: off operation 1=UPS is in is in off operation |  | 0 |  |  |  | ENUM |  |  | 1=UPS is in is in off operation
|  |  | 0 |  | UPS: battery operation | UPS: battery operation | TOO LONG | UPS: battery operation 2=UPS is in is in battery operation |  | 0 |  |  |  | ENUM |  |  | 2=UPS is in is in battery operation
|  |  | 0 |  | UPS: normal operation | UPS: normal operation | TOO LONG | UPS: normal operation 3=UPS is in is in normal operation |  | 0 |  |  |  | ENUM |  |  | 3=UPS is in is in normal operation
|  |  | 0 |  | UPS: forced static bypass operation | UPS: forced static bypass operation | TOO LONG | UPS: forced static bypass operation 4=UPS is in is in forced static bypass operation |  | 0 |  |  |  | ENUM |  |  | 4=UPS is in is in forced static bypass operation
|  |  | 0 |  | UPS: requested static bypass operation | UPS: requested static bypass operation | TOO LONG | UPS: requested static bypass operation 5=UPS is in is in requested static bypass operation |  | 0 |  |  |  | ENUM |  |  | 5=UPS is in is in requested static bypass operation
|  |  | 0 |  | UPS: maintenance bypass operation | UPS: maintenance bypass operation | TOO LONG | UPS: maintenance bypass operation 6=UPS is in maintenance bypass operation |  | 0 |  |  |  | ENUM |  |  | 6=UPS is in maintenance bypass operation
|  |  | 0 |  | UPS: emergency static bypass operation | UPS: emergency static bypass operation | TOO LONG | UPS: emergency static bypass operation 7=UPS is in emergency static bypass operation |  | 0 |  |  |  | ENUM |  |  | 7=UPS is in emergency static bypass operation
|  |  | 0 |  | UPS: inverter standby operation | UPS: inverter standby operation | TOO LONG | UPS: inverter standby operation 8=UPS is in inverter standby operation |  | 0 |  |  |  | ENUM |  |  | 8=UPS is in inverter standby operation
|  |  | 0 |  | UPS: static bypass standby operation | UPS: static bypass standby operation | TOO LONG | UPS: static bypass standby operation 9=UPS is in static bypass standby operation |  | 0 |  |  |  | ENUM |  |  | 9=UPS is in static bypass standby operation
|  |  | 0 |  | UPS: battery test | UPS: battery test | TOO LONG | UPS: battery test 10=UPS is in battery test |  | 0 |  |  |  | ENUM |  |  | 10=UPS is in battery test
|  |  | 0 |  | UPS: inverter SPoT mode | UPS: inverter SPoT mode | TOO LONG | UPS: inverter SPoT mode 11=UPS is in inverter SPoT mode |  | 0 |  |  |  | ENUM |  |  | 11=UPS is in inverter SPoT mode
|  |  | 0 |  | UPS: charger SPoT mode | UPS: charger SPoT mode | TOO LONG | UPS: charger SPoT mode 12=UPS is in charger SPoT mode |  | 0 |  |  |  | ENUM |  |  | 12=UPS is in charger SPoT mode
|  |  | 0 |  | UPS: battery SPoT mode | UPS: battery SPoT mode | TOO LONG | UPS: battery SPoT mode 13=UPS is in battery SPoT mode |  | 0 |  |  |  | ENUM |  |  | 13=UPS is in battery SPoT mode
|  |  | 0 |  | UPS: ECOnversion mode | UPS: ECOnversion mode | TOO LONG | UPS: ECOnversion mode 14=UPS is in ECOnversion mode |  | 0 |  |  |  | ENUM |  |  | 14=UPS is in ECOnversion mode
|  |  | 0 |  | UPS: ECO mode | UPS: ECO mode | 35 | UPS: ECO mode 15=UPS is in ECO mode |  | 0 |  |  |  | ENUM |  |  | 15=UPS is in ECO mode
45894 | 0x1705 | 5893 | 0 |  | UPS base model number check | UPS Model Number Check | 22 | UPS Model Number Check |  | 0 | 45894 |  | 1
|  |  | 0 |  | State is OK | State is OK | 25 | State is OK 0=State is OK |  | 0 |  |  |  | ENUM |  |  | 0=State is OK
|  |  | 0 |  | State is not OK | State is not OK | 33 | State is not OK 1=State is not OK |  | 0 |  |  |  | ENUM |  |  | 1=State is not OK
|  |  | 0 |  |  |  | 0 |  |  | 0
46145 | 0x1800 | 6144 | 0 |  | The present phase-to-phase input current in amperes in A (phase 1) | Phase A-B Input Current | 25 | Phase A-B Input Current A | Read Holding Registers | 0 | 46145 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | A
46146 | 0x1801 | 6145 | 0 |  | The present phase-to-phase input current in amperes in A (phase 2) | Phase B-C Input Current | 25 | Phase B-C Input Current A | Read Holding Registers | 0 | 46146 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | A
46147 | 0x1802 | 6146 | 0 |  | The present phase-to-phase input current in amperes in A (phase 3) | Phase C-A Input Current | 25 | Phase C-A Input Current A | Read Holding Registers | 0 | 46147 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | A
46148 | 0x1803 | 6147 | 0 |  | The present phase-to-phase bypass current in amperes in A (phase 1) | Phase A-B Bypass Current | 26 | Phase A-B Bypass Current A | Read Holding Registers | 0 | 46148 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | A
46149 | 0x1804 | 6148 | 0 |  | The present phase-to-phase bypass current in amperes in A (phase 2) | Phase B-C Bypass Current | 26 | Phase B-C Bypass Current A | Read Holding Registers | 0 | 46149 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | A
46150 | 0x1805 | 6149 | 0 |  | The present phase-to-phase bypass current in amperes in A (phase 3) | Phase C-A Bypass Current | 26 | Phase C-A Bypass Current A | Read Holding Registers | 0 | 46150 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | A
46151 | 0x1806 | 6150 | 0 |  | The present phase-to-phase output current in amperes in A (phase 1) | Phase A-B Output Current | 26 | Phase A-B Output Current A | Read Holding Registers | 0 | 46151 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | A
46152 | 0x1807 | 6151 | 0 |  | The present phase-to-phase output current in amperes in A (phase 2) | Phase B-C Output Current | 26 | Phase B-C Output Current A | Read Holding Registers | 0 | 46152 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | A
46153 | 0x1808 | 6152 | 0 |  | The present phase-to-phase output current in amperes in A (phase 3) | Phase C-A Output Current | 26 | Phase C-A Output Current A | Read Holding Registers | 0 | 46153 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | A
46154 | 0x1809 | 6153 | 0 |  | The present total apparent output power (for all three phases) for the parallel system | Total Parallel Apparent Output Power | 40 | Total Parallel Apparent Output Power kVA | Read Holding Registers | 0 | 46154 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | kVA
46155 | 0x180A | 6154 | 0 |  | The percentage of the UPS system capacity presently used across all phases. The load percentage for the highest phase load is displayed | Usage of UPS System Capacity | 30 | Usage of UPS System Capacity % | Read Holding Registers | 0 | 46155 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | %
46156 | 0x180B | 6155 | 0 |  | The present total active output power (for all three phases) for the parallel system | Total Active Output Power | 28 | Total Active Output Power kW | Read Holding Registers | 0 | 46156 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | kW
|  |  | 0 |  |  |  | 0 |  |  | 0
46401 | 0x1900 | 6400 | 0 |  | The temperature measured by the sensor | Temperature Sensor | 21 | Temperature Sensor °C | Read Holding Registers | 0 | 46401 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | °C
46402 | 0x1901 | 6401 | 0 |  | The humidity measured by the sensor | Humidity Sensor | 20 | Humidity Sensor % RH | Read Holding Registers | 0 | 46402 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | % RH
|  |  | 0 |  |  |  | 0 |  |  | 0
|  |  | 0 |  |  |  | 0 |  |  | 0
|  |  | 0 |  |  |  | 0 |  |  | 0
Configuration Data |  |  | 0 |  |  |  | 0 |  |  | 0
48193 | 0x2000 | 8192 | 0 |  | This is the configured AC voltage system setting. The setting applies for input as well if no specific setting is placed in input system. | AC Voltage System Setting | 25 | AC Voltage System Setting |  | 0 | 48193 |  | 1
|  |  | 0 |  | Output voltage 380VAC PhPh | Output voltage 380VAC PhPh | TOO LONG | Output voltage 380VAC PhPh 0=Output voltage 380VAC PhPh |  | 0 |  |  |  | ENUM |  |  | 0=Output voltage 380VAC PhPh
|  |  | 0 |  | Output voltage 400VAC PhPh | Output voltage 400VAC PhPh | TOO LONG | Output voltage 400VAC PhPh 1=Output voltage 400VAC PhPh |  | 0 |  |  |  | ENUM |  |  | 1=Output voltage 400VAC PhPh
|  |  | 0 |  | Output voltage 415VAC PhPh | Output voltage 415VAC PhPh | TOO LONG | Output voltage 415VAC PhPh 2=Output voltage 415VAC PhPh |  | 0 |  |  |  | ENUM |  |  | 2=Output voltage 415VAC PhPh
|  |  | 0 |  | Output voltage 480VAC PhPh | Output voltage 480VAC PhPh | TOO LONG | Output voltage 480VAC PhPh 3=Output voltage 480VAC PhPh |  | 0 |  |  |  | ENUM |  |  | 3=Output voltage 480VAC PhPh
|  |  | 0 |  | Output voltage 208VAC PhPh | Output voltage 208VAC PhPh | TOO LONG | Output voltage 208VAC PhPh 4=Output voltage 208VAC PhPh |  | 0 |  |  |  | ENUM |  |  | 4=Output voltage 208VAC PhPh
|  |  | 0 |  | Output voltage 200VAC PhPh | Output voltage 200VAC PhPh | TOO LONG | Output voltage 200VAC PhPh 5=Output voltage 200VAC PhPh |  | 0 |  |  |  | ENUM |  |  | 5=Output voltage 200VAC PhPh
|  |  | 0 |  | Output voltage 220VAC PhPh | Output voltage 220VAC PhPh | TOO LONG | Output voltage 220VAC PhPh 6=Output voltage 220VAC PhPh |  | 0 |  |  |  | ENUM |  |  | 6=Output voltage 220VAC PhPh
|  |  | 0 |  | Output voltage 440VAC PhPh | Output voltage 440VAC PhPh | TOO LONG | Output voltage 440VAC PhPh 7=Output voltage 440VAC PhPh |  | 0 |  |  |  | ENUM |  |  | 7=Output voltage 440VAC PhPh
48194 | 0x2001 | 8193 | 0 |  | Setting for single mains or dual mains supply | Single Mains or Dual Mains | 26 | Single Mains or Dual Mains |  | 0 | 48194 |  | 1
|  |  | 0 |  | Single mains system | Single mains system | TOO LONG | Single mains system 0=Single mains system |  | 0 |  |  |  | ENUM |  |  | 0=Single mains system
|  |  | 0 |  | Dual mains system | Dual mains system | 37 | Dual mains system 1=Dual mains system |  | 0 |  |  |  | ENUM |  |  | 1=Dual mains system
48195 | 0x2002 | 8194 | 0 |  | Ramp in timer for input current limitation during transfer from battery to normal operation | Transfer Current Ramp-in Timer | 34 | Transfer Current Ramp-in Timer Sec | Read Holding Registers | 0 | 48195 | Unsigned 16 bit Integer | 1 | UINT16 |  |  | Sec
48196 | 0x2003 | 8195 | 0 |  | Defines the AC wiring of the system: 3-wire does not include neutral; 4-wire includes neutral | AC Wiring Config ABC ABCN | 25 | AC Wiring Config ABC ABCN |  | 0 | 48196 |  | 1
|  |  | 0 |  | 3-wire system configuration | 3-wire system configuration | TOO LONG | 3-wire system configuration 0=3 wire-system configuration |  | 0 |  |  |  | ENUM |  |  | 0=3 wire-system configuration
|  |  | 0 |  | 4-wire system configuration | 4-wire system configuration | TOO LONG | 4-wire system configuration 1=4 wire-system configuration |  | 0 |  |  |  | ENUM |  |  | 1=4 wire-system configuration
|  |  | 0 |  | 4-wire system configuration HRG | 4-wire system configuration HRG | TOO LONG | 4-wire system configuration HRG 2=4-wire system configuration HRG |  | 0 |  |  |  | ENUM |  |  | 2=4-wire system configuration HRG
48197 | 0x2004 | 8196 | 0 |  | Energy storage type | Energy Storage Type | 19 | Energy Storage Type |  | 0 | 48197 |  | 1
|  |  | 0 |  | No energy storage | No energy storage | 37 | No energy storage 0=No energy storage |  | 0 |  |  |  | ENUM |  |  | 0=No energy storage
|  |  | 0 |  | Battery/batteries | Battery/batteries | 37 | Battery/batteries 1=Battery/batteries |  | 0 |  |  |  | ENUM |  |  | 1=Battery/batteries
|  |  | 0 |  | Flywheel | Flywheel | 19 | Flywheel 2=Flywheel |  | 0 |  |  |  | ENUM |  |  | 2=Flywheel
|  |  | 0 |  | Ultra capacitors | Ultra capacitors | 35 | Ultra capacitors 3=Ultra capacitors |  | 0 |  |  |  | ENUM |  |  | 3=Ultra capacitors
48198 | 0x2005 | 8197 | 0 |  | Voltage compensation. Increase voltage to compensate for different cable lengths | Voltage Compensation | 22 | Voltage Compensation % | Read Holding Registers | 0 | 48198 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | %
48199 | 0x2006 | 8198 | 0 |  | This is the output frequency setting including the tolerance. This drives whether the output is in sync with the input. | Output Frequency Sync Setting | 29 | Output Frequency Sync Setting |  | 0 | 48199 |  | 1
|  |  | 0 |  | Frequency of 50 Hz +/- 1.0 Hz. | Frequency of 50 Hz +/- 1.0 Hz. | TOO LONG | Frequency of 50 Hz +/- 1.0 Hz. 0=Frequency of 50 Hz +/- 1.0 Hz. |  | 0 |  |  |  | ENUM |  |  | 0=Frequency of 50 Hz +/- 1.0 Hz.
|  |  | 0 |  | Frequency of 50 Hz +/- 3.0 Hz. | Frequency of 50 Hz +/- 3.0 Hz. | TOO LONG | Frequency of 50 Hz +/- 3.0 Hz. 1=Frequency of 50 Hz +/- 3.0 Hz. |  | 0 |  |  |  | ENUM |  |  | 1=Frequency of 50 Hz +/- 3.0 Hz.
|  |  | 0 |  | Frequency of 60 Hz +/- 1.0 Hz. | Frequency of 60 Hz +/- 1.0 Hz. | TOO LONG | Frequency of 60 Hz +/- 1.0 Hz. 2=Frequency of 60 Hz +/- 1.0 Hz. |  | 0 |  |  |  | ENUM |  |  | 2=Frequency of 60 Hz +/- 1.0 Hz.
|  |  | 0 |  | Frequency of 60 Hz +/- 3.0 Hz. | Frequency of 60 Hz +/- 3.0 Hz. | TOO LONG | Frequency of 60 Hz +/- 3.0 Hz. 3=Frequency of 60 Hz +/- 3.0 Hz. |  | 0 |  |  |  | ENUM |  |  | 3=Frequency of 60 Hz +/- 3.0 Hz.
|  |  | 0 |  | Frequency of 50 Hz +/- 10.0 Hz. | Frequency of 50 Hz +/- 10.0 Hz. | TOO LONG | Frequency of 50 Hz +/- 10.0 Hz. 4=Frequency of 50 Hz +/- 10.0 Hz. |  | 0 |  |  |  | ENUM |  |  | 4=Frequency of 50 Hz +/- 10.0 Hz.
|  |  | 0 |  | Frequency of 60 Hz +/- 10.0 Hz. | Frequency of 60 Hz +/- 10.0 Hz. | TOO LONG | Frequency of 60 Hz +/- 10.0 Hz. 5=Frequency of 60 Hz +/- 10.0 Hz. |  | 0 |  |  |  | ENUM |  |  | 5=Frequency of 60 Hz +/- 10.0 Hz.
48200 | 0x2007 | 8199 | 0 |  | The UPS power rating (kVA). | UPS Apparent Power Rating | 29 | UPS Apparent Power Rating kVA | Read Holding Registers | 0 | 48200 | Unsigned 16 bit Integer | 1 | UINT16 |  |  | kVA
48201 | 0x2008 | 8200 | 0 |  | Acceptable voltage as percent of nominal voltage (voltage tolerance) | Acceptable Percent of Nominal Voltage | 39 | Acceptable Percent of Nominal Voltage % | Read Holding Registers | 0 | 48201 | Unsigned 16 bit Integer | 1 | UINT16 |  |  | %
48202 | 0x2009 | 8201 | 0 |  | Delay time before autostart of the inverter after input source returns after an outage | Inverter Autostart Delay Time | 29 | Inverter Autostart Delay Time |  | 0 | 48202 |  | 1
|  |  | 0 |  | Function disabled | Function disabled | 37 | Function disabled 0=Function disabled |  | 0 |  |  |  | ENUM |  |  | 0=Function disabled
|  |  | 0 |  | Function enabled | Function enabled | 35 | Function enabled 1=Function enabled |  | 0 |  |  |  | ENUM |  |  | 1=Function enabled
48203 | 0x200A | 8202 | 0 |  | Set user-defined threshold for output overload status. | Set Output Overload Status Threshold | 38 | Set Output Overload Status Threshold % | Read Holding Registers | 0 | 48203 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | %
48204 | 0x200B | 8203 | 0 |  | Settings for autoboost mode of the charger | Charger Autoboost Settings | 26 | Charger Autoboost Settings |  | 0 | 48204 |  | 1
|  |  | 0 |  | Disable autoboost charger | Disable autoboost charger | TOO LONG | Disable autoboost charger 0=Disable autoboost charger |  | 0 |  |  |  | ENUM |  |  | 0=Disable autoboost charger
|  |  | 0 |  | Enable autoboost charger | Enable autoboost charger | TOO LONG | Enable autoboost charger 1=Enable autoboost charger |  | 0 |  |  |  | ENUM |  |  | 1=Enable autoboost charger
48205 | 0x200C | 8204 | 0 |  | Setting for charge current rate by user | Charger Current Rate User Settings | 34 | Charger Current Rate User Settings | Read Holding Registers | 0 | 48205 | Unsigned 16 bit Integer | 1 | UINT16 | 0.01 | 100
48206 | 0x200D | 8205 | 0 |  | Setting for auto cyclic mode charge mode | Setting for auto cyclic mode charge mode | 40 | Setting for auto cyclic mode charge mode |  | 0 | 48206 |  | 1
|  |  | 0 |  | Function disabled | Function disabled | 37 | Function disabled 0=Function disabled |  | 0 |  |  |  | ENUM |  |  | 0=Function disabled
|  |  | 0 |  | Function enabled | Function enabled | 35 | Function enabled 1=Function enabled |  | 0 |  |  |  | ENUM |  |  | 1=Function enabled
48207 | 0x200E | 8206 | 0 |  | Configuration of breakers | Breaker Configuration 1 | 23 | Breaker Configuration 1 |  | 0 | 48207 |  | 1
|  |  | 0 |  | Not present | Not present | 25 | Not present 0=Not present |  | 0 |  |  |  | ENUM |  |  | 0=Not present
|  |  | 0 |  | Present | Present | 17 | Present 1=Present |  | 0 |  |  |  | ENUM |  |  | 1=Present
48208 | 0x200F | 8207 | 0 |  | Configuration of breakers | Breaker Configuration 2 | 23 | Breaker Configuration 2 |  | 0 | 48208 |  | 1
|  |  | 0 |  | Not present | Not present | 25 | Not present 0=Not present |  | 0 |  |  |  | ENUM |  |  | 0=Not present
|  |  | 0 |  | Present | Present | 17 | Present 1=Present |  | 0 |  |  |  | ENUM |  |  | 1=Present
48209 | 0x2010 | 8208 | 0 |  | Battery deep discharge settings. | Battery Deep Discharge Settings | 31 | Battery Deep Discharge Settings |  | 0 | 48209 |  | 1
|  |  | 0 |  | Deep discharge is not allowed. | Deep discharge is not allowed. | TOO LONG | Deep discharge is not allowed. 0=Deep discharge is not allowed. |  | 0 |  |  |  | ENUM |  |  | 0=Deep discharge is not allowed.
|  |  | 0 |  | Deep discharge is allowed. | Deep discharge is allowed. | TOO LONG | Deep discharge is allowed. 1=Deep discharge is allowed. |  | 0 |  |  |  | ENUM |  |  | 1=Deep discharge is allowed.
48210 | 0x2011 | 8209 | 0 |  | Setting for minimum allowed temperature | Minimum Allow Tempurature Setting | 36 | Minimum Allow Tempurature Setting °C | Read Holding Registers | 0 | 48210 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | °C
48211 | 0x2012 | 8210 | 0 |  | Setting for maximum allowed temperature | Maximum Allow Tempurature Setting | 36 | Maximum Allow Tempurature Setting °C | Read Holding Registers | 0 | 48211 | Unsigned 16 bit Integer | 1 | UINT16 | 0.1 | 10 | °C
48212 | 0x2013 | 8211 | 0 |  | Battery solution setting for predefined battery solutions | Battery Solution Setting | 24 | Battery Solution Setting |  | 0 | 48212 |  | 1
|  |  | 0 |  | Custom battery solution | Custom battery solution | TOO LONG | Custom battery solution 0=Custom battery solution |  | 0 |  |  |  | ENUM |  |  | 0=Custom battery solution
|  |  | 0 |  | Battery solution type GVSCBC7A | Battery solution type GVSCBC7A | TOO LONG | Battery solution type GVSCBC7A 1=Battery solution type GVSCBC7A |  | 0 |  |  |  | ENUM |  |  | 1=Battery solution type GVSCBC7A
|  |  | 0 |  | Battery solution type GVSCBC7B | Battery solution type GVSCBC7B | TOO LONG | Battery solution type GVSCBC7B 2=Battery solution type GVSCBC7B |  | 0 |  |  |  | ENUM |  |  | 2=Battery solution type GVSCBC7B
|  |  | 0 |  | Battery solution type GVSCBC7C | Battery solution type GVSCBC7C | TOO LONG | Battery solution type GVSCBC7C 3=Battery solution type GVSCBC7C |  | 0 |  |  |  | ENUM |  |  | 3=Battery solution type GVSCBC7C
|  |  | 0 |  | Battery solution type GVSCBC10A/GVSCBC10A2 | Battery solution type GVSCBC10A/GVSCBC10A2 | TOO LONG | Battery solution type GVSCBC10A/GVSCBC10A2 4=Battery solution type GVSCBC10A/GVSCBC10A2 |  | 0 |  |  |  | ENUM |  |  | 4=Battery solution type GVSCBC10A/GVSCBC10A2
|  |  | 0 |  | Battery solution type GVSCBC10B/GVSCBC10B2 | Battery solution type GVSCBC10B/GVSCBC10B2 | TOO LONG | Battery solution type GVSCBC10B/GVSCBC10B2 5=Battery solution type GVSCBC10B/GVSCBC10B2 |  | 0 |  |  |  | ENUM |  |  | 5=Battery solution type GVSCBC10B/GVSCBC10B2
|  |  | 0 |  | Battery solution type GVSCBT1/GVSCBT1ST | Battery solution type GVSCBT1/GVSCBT1ST | TOO LONG | Battery solution type GVSCBT1/GVSCBT1ST 6=Battery solution type GVSCBT1/GVSCBT1ST |  | 0 |  |  |  | ENUM |  |  | 6=Battery solution type GVSCBT1/GVSCBT1ST
|  |  | 0 |  | Battery solution type GVSCBT2/GVSCBT2ST | Battery solution type GVSCBT2/GVSCBT2ST | TOO LONG | Battery solution type GVSCBT2/GVSCBT2ST 7=Battery solution type GVSCBT2/GVSCBT2ST |  | 0 |  |  |  | ENUM |  |  | 7=Battery solution type GVSCBT2/GVSCBT2ST
|  |  | 0 |  | Battery solution type GVSCBT3/GVSCBT3ST | Battery solution type GVSCBT3/GVSCBT3ST | TOO LONG | Battery solution type GVSCBT3/GVSCBT3ST 8=Battery solution type GVSCBT3/GVSCBT3ST |  | 0 |  |  |  | ENUM |  |  | 8=Battery solution type GVSCBT3/GVSCBT3ST
|  |  | 0 |  | Battery solution type GVSCBT4/GVSCBT4ST | Battery solution type GVSCBT4/GVSCBT4ST | TOO LONG | Battery solution type GVSCBT4/GVSCBT4ST 9=Battery solution type GVSCBT4/GVSCBT4ST |  | 0 |  |  |  | ENUM |  |  | 9=Battery solution type GVSCBT4/GVSCBT4ST
|  |  | 0 |  | Battery solution type GVSCBT5/GVSCBT5ST | Battery solution type GVSCBT5/GVSCBT5ST | TOO LONG | Battery solution type GVSCBT5/GVSCBT5ST 10=Battery solution type GVSCBT5/GVSCBT5ST |  | 0 |  |  |  | ENUM |  |  | 10=Battery solution type GVSCBT5/GVSCBT5ST
|  |  | 0 |  | Battery solution type LIBATTSMGEIEC | Battery solution type LIBATTSMGEIEC | TOO LONG | Battery solution type LIBATTSMGEIEC 11=Battery solution type LIBATTSMGEIEC |  | 0 |  |  |  | ENUM |  |  | 11=Battery solution type LIBATTSMGEIEC
|  |  | 0 |  | Battery solution type LIBATTSMGEUL | Battery solution type LIBATTSMGEUL | TOO LONG | Battery solution type LIBATTSMGEUL 12=Battery solution type LIBATTSMGEUL |  | 0 |  |  |  | ENUM |  |  | 12=Battery solution type LIBATTSMGEUL
|  |  | 0 |  | Modular battery solution | Modular battery solution | TOO LONG | Modular battery solution 13=Modular battery solution |  | 0 |  |  |  | ENUM |  |  | 13=Modular battery solution
|  |  | 0 |  | Battery solution type GVSCBT6ST | Battery solution type GVSCBT6ST | TOO LONG | Battery solution type GVSCBT6ST 14=Battery solution type GVSCBT6ST |  | 0 |  |  |  | ENUM |  |  | 14=Battery solution type GVSCBT6ST
|  |  | 0 |  | Battery solution type GVSCBT7ST | Battery solution type GVSCBT7ST | TOO LONG | Battery solution type GVSCBT7ST 15=Battery solution type GVSCBT7ST |  | 0 |  |  |  | ENUM |  |  | 15=Battery solution type GVSCBT7ST
48213 | 0x2014 | 8212 | 0 |  | Setting for automatic test | Automatic Test Setting | 22 | Automatic Test Setting |  | 0 | 48213 |  | 1
|  |  | 0 |  | Never autotest | Never autotest | 31 | Never autotest 0=Never autotest |  | 0 |  |  |  | ENUM |  |  | 0=Never autotest
|  |  | 0 |  | Autotest every week | Autotest every week | TOO LONG | Autotest every week 1=Autotest every week |  | 0 |  |  |  | ENUM |  |  | 1=Autotest every week
|  |  | 0 |  | Autotest every 2 week | Autotest every 2 week | TOO LONG | Autotest every 2 week 2=Autotest every 2 week |  | 0 |  |  |  | ENUM |  |  | 2=Autotest every 2 week
|  |  | 0 |  | Autotest every 4 week | Autotest every 4 week | TOO LONG | Autotest every 4 week 3=Autotest every 4 week |  | 0 |  |  |  | ENUM |  |  | 3=Autotest every 4 week
|  |  | 0 |  | Autotest every 8 week | Autotest every 8 week | TOO LONG | Autotest every 8 week 4=Autotest every 8 week |  | 0 |  |  |  | ENUM |  |  | 4=Autotest every 8 week
|  |  | 0 |  | Autotest every 12 week | Autotest every 12 week | TOO LONG | Autotest every 12 week 5=Autotest every 12 week |  | 0 |  |  |  | ENUM |  |  | 5=Autotest every 12 week
|  |  | 0 |  | Autotest every 26 week | Autotest every 26 week | TOO LONG | Autotest every 26 week 6=Autotest every 26 week |  | 0 |  |  |  | ENUM |  |  | 6=Autotest every 26 week
|  |  | 0 |  | Autotest every 52 week | Autotest every 52 week | TOO LONG | Autotest every 52 week 7=Autotest every 52 week |  | 0 |  |  |  | ENUM |  |  | 7=Autotest every 52 week
48214 | 0x2015 | 8213 | 8214 |  | Time of day battery test should start. The min should be 0 the max should be 86399 (24 hours). | Battery Test Sched. Time of Day | 35 | Battery Test Sched. Time of Day Sec | Read Holding Registers | 48215 | 48214 | Unsigned 32 bit Integer | 2 | UINT32 | 1 | 1 | Sec
48216 | 0x2017 | 8215 | 0 |  | Day of week battery test should start | Battery Test Sched. Day of Week | 31 | Battery Test Sched. Day of Week |  | 0 | 48216 |  | 1
|  |  | 0 |  | Test on Monday | Test on Monday | 31 | Test on Monday 0=Test on Monday |  | 0 |  |  |  | ENUM |  |  | 0=Test on Monday
|  |  | 0 |  | Test on Tuesday | Test on Tuesday | 33 | Test on Tuesday 1=Test on Tuesday |  | 0 |  |  |  | ENUM |  |  | 1=Test on Tuesday
|  |  | 0 |  | Test on Wednesday | Test on Wednesday | 37 | Test on Wednesday 2=Test on Wednesday |  | 0 |  |  |  | ENUM |  |  | 2=Test on Wednesday
|  |  | 0 |  | Test on Thursday | Test on Thursday | 35 | Test on Thursday 3=Test on Thursday |  | 0 |  |  |  | ENUM |  |  | 3=Test on Thursday
|  |  | 0 |  | Test on Friday | Test on Friday | 31 | Test on Friday 4=Test on Friday |  | 0 |  |  |  | ENUM |  |  | 4=Test on Friday
|  |  | 0 |  | Test on Saturday | Test on Saturday | 35 | Test on Saturday 5=Test on Saturday |  | 0 |  |  |  | ENUM |  |  | 5=Test on Saturday
|  |  | 0 |  | Test on Sunday | Test on Sunday | 31 | Test on Sunday 6=Test on Sunday |  | 0 |  |  |  | ENUM |  |  | 6=Test on Sunday
48217 | 0x2018 | 8216 | 0 |  | Switchgear system setting | System Switchgear Setting | 25 | System Switchgear Setting |  | 0 | 48217 |  | 1
|  |  | 0 | 0 | Unit input breaker (UIB) setting | Unit input breaker (UIB) setting | TOO LONG | Unit input breaker (UIB) setting 1=Present |  | 0 |  |  |  | BOOLEAN |  |  | 1=Present
|  |  | 0 | 1 | Unit output breaker (UOB) setting | Unit output breaker (UOB) setting | TOO LONG | Unit output breaker (UOB) setting 1=Present |  | 0 |  |  |  | BOOLEAN |  |  | 1=Present
|  |  | 0 | 2 | Static switch input breaker (SSIB) setting | Static switch input breaker (SSIB) setting | TOO LONG | Static switch input breaker (SSIB) setting 1=Present |  | 0 |  |  |  | BOOLEAN |  |  | 1=Present
|  |  | 0 | 3 | Maintenance bypass breaker (MBB) setting | Maintenance bypass breaker (MBB) setting | TOO LONG | Maintenance bypass breaker (MBB) setting 1=Present |  | 0 |  |  |  | BOOLEAN |  |  | 1=Present
|  |  | 0 | 4 | Redundant internal maintenance breaker (RIMB) setting | Redundant internal maintenance breaker (RIMB) setting | TOO LONG | Redundant internal maintenance breaker (RIMB) setting 1=Present |  | 0 |  |  |  | BOOLEAN |  |  | 1=Present
|  |  | 0 | 5 | System isolation breaker (SIB) setting | System isolation breaker (SIB) setting | TOO LONG | System isolation breaker (SIB) setting 1=Present |  | 0 |  |  |  | BOOLEAN |  |  | 1=Present
48218 | 0x2019 | 8217 | 0 |  | Slew rate of the inverter | Inverter Slew Rate | 18 | Inverter Slew Rate |  | 0 | 48218 |  | 1
|  |  | 0 |  | Slew rate is 0.25 Hz/s | Slew rate is 0.25 Hz/s | TOO LONG | Slew rate is 0.25 Hz/s 0=Slew rate is 0.25 Hz/s |  | 0 |  |  |  | ENUM |  |  | 0=Slew rate is 0.25 Hz/s
|  |  | 0 |  | Slew rate is 0.50 Hz/s | Slew rate is 0.50 Hz/s | TOO LONG | Slew rate is 0.50 Hz/s 1=Slew rate is 0.50 Hz/s |  | 0 |  |  |  | ENUM |  |  | 1=Slew rate is 0.50 Hz/s
|  |  | 0 |  | Slew rate is 1 Hz/s | Slew rate is 1 Hz/s | TOO LONG | Slew rate is 1 Hz/s 2=Slew rate is 1 Hz/s |  | 0 |  |  |  | ENUM |  |  | 2=Slew rate is 1 Hz/s
|  |  | 0 |  | Slew rate is 2 Hz/s | Slew rate is 2 Hz/s | TOO LONG | Slew rate is 2 Hz/s 3=Slew rate is 2 Hz/s |  | 0 |  |  |  | ENUM |  |  | 3=Slew rate is 2 Hz/s
|  |  | 0 |  | Slew rate is 4 Hz/s | Slew rate is 4 Hz/s | TOO LONG | Slew rate is 4 Hz/s 4=Slew rate is 4 Hz/s |  | 0 |  |  |  | ENUM |  |  | 4=Slew rate is 4 Hz/s
|  |  | 0 |  | Slew rate is 6 Hz/s | Slew rate is 6 Hz/s | TOO LONG | Slew rate is 6 Hz/s 5=Slew rate is 6 Hz/s |  | 0 |  |  |  | ENUM |  |  | 5=Slew rate is 6 Hz/s
48219 | 0x201A | 8218 | 0 |  | Setting for adjusting the output voltage to compensate for load dependant transformer voltage drop. It must be synchronized in parallel systems. | Transformer Voltage Drop Compensation | 39 | Transformer Voltage Drop Compensation % | Read Holding Registers | 0 | 48219 | Unsigned 16 bit Integer | 1 | UINT16 |  |  | %
48220 | 0x201B | 8219 | 0 |  | Setting to configure break duration in ms. when shifting to an asynchronous bypass. | Asynch. Bypass Brk Duration Setting | 38 | Asynch. Bypass Brk Duration Setting ms | Read Holding Registers | 0 | 48220 | Unsigned 16 bit Integer | 1 | UINT16 | 1 | 1 | ms
48221 | 0x201C | 8220 | 0 |  | The charging capacity based on system kW rating. | Charging Capacity from System Rated kW | 40 | Charging Capacity from System Rated kW % | Read Holding Registers | 0 | 48221 | Unsigned 16 bit Integer | 1 | UINT16 | 1 | 1 | %
48222 | 0x201D | 8221 | 0 |  | The number of modular battery cabinets connected to the UPS. | UPS Modular Battery Cabinets | 28 | UPS Modular Battery Cabinets | Read Holding Registers | 0 | 48222 | Unsigned 16 bit Integer | 1 | UINT16
48223 | 0x201E | 8222 | 0 |  | The parallel UPS number of the operated UPS. | Parallel UPS Number of the Operated UPS | 39 | Parallel UPS Number of the Operated UPS | Read Holding Registers | 0 | 48223 | Unsigned 16 bit Integer | 1 | UINT16 | 1 | 1
48224 | 0x201F | 8223 | 0 |  | Setting for which parallel UPSs are present in the system. Each UPS can be selected as present or not present. | Parallel UPS Present in System | 30 | Parallel UPS Present in System |  | 0 | 48224 |  | 1
|  |  | 0 | 0 | unit_1 | unit_1 | 16 | unit_1 1=Present |  | 0 |  |  |  | BOOLEAN |  |  | 1=Present
|  |  | 0 | 1 | unit_2 | unit_2 | 16 | unit_2 1=Present |  | 0 |  |  |  | BOOLEAN |  |  | 1=Present
|  |  | 0 | 2 | unit_3 | unit_3 | 16 | unit_3 1=Present |  | 0 |  |  |  | BOOLEAN |  |  | 1=Present
|  |  | 0 | 3 | unit_4 | unit_4 | 16 | unit_4 1=Present |  | 0 |  |  |  | BOOLEAN |  |  | 1=Present
48225 | 0x2020 | 8224 | 0 |  | The selected number of redundant UPSs in the parallel system. | Parallel UPS Number of Redundant UPS | 36 | Parallel UPS Number of Redundant UPS |  | 0 | 48225 |  | 1
|  |  | 0 |  | N+0 | N+0 | 9 | N+0 0=N+0 |  | 0 |  |  |  | ENUM |  |  | 0=N+0
|  |  | 0 |  | N+1 | N+1 | 9 | N+1 1=N+1 |  | 0 |  |  |  | ENUM |  |  | 1=N+1
|  |  | 0 |  | N+2 | N+2 | 9 | N+2 2=N+2 |  | 0 |  |  |  | ENUM |  |  | 2=N+2
|  |  | 0 |  | N+3 | N+3 | 9 | N+3 3=N+3 |  | 0 |  |  |  | ENUM |  |  | 3=N+3
48226 | 0x2021 | 8225 | 0 |  | The minimum number of parallel units available to start up automatically. | Parallel UPS Min. Avail. for Autostart | 38 | Parallel UPS Min. Avail. for Autostart | Read Holding Registers | 0 | 48226 | Unsigned 16 bit Integer | 1 | UINT16 | 1 | 1
48227 | 0x2022 | 8226 | 0 |  | Status to indicate whether there are enough UPSs for the parallel system to enter the inverter operation mode. | Parallel UPS Qty Check for Invert. Mode | 39 | Parallel UPS Qty Check for Invert. Mode |  | 0 | 48227 |  | 1
|  |  | 0 |  | State is OK | State is OK | 25 | State is OK 0=State is OK |  | 0 |  |  |  | ENUM |  |  | 0=State is OK
|  |  | 0 |  | State is not OK | State is not OK | 33 | State is not OK 1=State is not OK |  | 0 |  |  |  | ENUM |  |  | 1=State is not OK
48228 | 0x2023 | 8227 | 0 |  | Current UPS power rating (kW). | UPS Real Power Rating | 24 | UPS Real Power Rating kW | Read Holding Registers | 0 | 48228 | Unsigned 16 bit Integer | 1 | UINT16 |  |  | kW
48229 | 0x2024 | 8228 | 0 |  | Battery type of the connected batteries | Battery Type of Batteries | 25 | Battery Type of Batteries |  | 0 | 48229 |  | 1
|  |  | 0 |  | Valve-regulated lead-acid, or maintenance-free | Valve-regulated lead-acid, or maintenance-free | TOO LONG | Valve-regulated lead-acid, or maintenance-free 0=Valve-regulated lead-acid or maintenance-free battery type |  | 0 |  |  |  | ENUM |  |  | 0=Valve-regulated lead-acid or maintenance-free battery type
|  |  | 0 |  | Vented, flooded, wet, or open cell | Vented, flooded, wet, or open cell | TOO LONG | Vented, flooded, wet, or open cell 1=Vented, flooded, wet, or open cell battery type |  | 0 |  |  |  | ENUM |  |  | 1=Vented, flooded, wet, or open cell battery type
|  |  | 0 |  | Lithium-ion | Lithium-ion | 38 | Lithium-ion 2=Lithium-ion battery type |  | 0 |  |  |  | ENUM |  |  | 2=Lithium-ion battery type
|  |  | 0 |  | NiCd | NiCd | 24 | NiCd 3=NiCd battery type |  | 0 |  |  |  | ENUM |  |  | 3=NiCd battery type
Worldwide Customer Support Customer support for this or any other product is available at no charge in any of the following ways: *Visit the Schneider Electric Web site to access documents in the Schneider Electric Knowledge Base and to submit customer support requests. –www.schneider-electric.com (Corporate Headquarters) Connect to localized Schneider Electric Web sites for specific countries, each of which provides customer support information. – www.schneider-electric.com/support/ Global support searching Schneider Electric Knowledge Base and using e-support. *Contact the Schneider Electric Customer Support Center by telephone or e-mail. –Local, country-specific centers: go to www.schneider-electric.com > Support > Operations around the world for contact information. For information on how to obtain local customer support, contact the representative or other distributors from whom you purchased your product. © 2020 Schneider Electric, All Rights Reserved. Schneider Electric, and network management card are trademarks and the property of Schneider Electric SE, its subsidiaries and affiliated companies. All other trademarks are property of their respective owners. |  |  | 0 |  |  | 0 | 1 | 0 |  | 0